Industrial Managed Ethernet Switch User Manual – Layers 2 & 3

_______________________________________________________________________________

Firmware Version 1.2.45 User Manual Compliant: For Military contracts that require the continuous monitoring and protection of industrial control systems (ICS) Networks Operating / monitoring the operating utilities such as Water, Sewer, Electrical, Security, Video, Building Controls, Street, and Intelligent Transportation Systems (ITS). Uses: Cyber-Lock, IP Device Binding, Cyber-Secure Video, Clean Code Technology, & Secure Console / Chassis (Patent Pending) Meets NSA Guidelines for Secure Network Endpoints

Copyright DYMEC 2021 – All Rights Reserved

DYMEC Series Layer 3 Switches

_______________________________________________________________________________

DYMEC Models Covered by This Manual

Specifications Subject to Change at the Direction of DYMEC

| 0802 Series: | KY-CPG0802, KY-CSX0802 |
| --- | --- |
| 0804 Series: | KY-CPG0804, KY-CPX0804, KY-CTG0804 |
| 1002 Series: | KY-CSG1002 |
| 1604 Series: | KY-CSX1604, KY-CPX1604 KY-CP1604GB, KY-CP1604XB |
| 2404 Series: 3170 Series | KY-CS2404GS-8C, KY-CSX2404 KY-CPG2404, KY-CPX2404 KY-3170XR |

| Models Covered by This Manual |  |
| --- | --- |

Content

Overview	4

Basic Settings

System	9

IPv4 (VLAN IP)	10

IPv6 (VLAN IP)	12

System Time	13

Precision Time Protocol (PTP)	15

Redundancy

Spanning Tree	21

ERPS	30

MRP	36

Management

SNMP	41

DHCP	46

PoE	53

Industrial Protocols	59

UPnP	75

L2 Switching

Port Management	76

IGMP Snooping	85

802.1Q VLAN	89

Quality of Service	94

Port Trunk	98

L3 Routing

Static Route	100

OSPFv2	106

OSPFv3	115

RIPv1/v2	118

RIPng	127

VRRP	130

Security

Storm Control	133

802.1X	134

Service Control	138

Access Control List	140

SSH	143

Diagnostics

Port Mirroring	145

Ping	146

Cable Diagnostic	148

Monitoring

LLDP	149

System Warning	151

Data Collection	157

MAC Table	162

Maintenance

Authorization	164

Firmware Upgrade	168

Config Backup	172

Config Restore	173

USB Auto-Load & Auto-Backup	174

SFTP File Access	175

Command Line Interface

Connect to CLI via Console Port	176

Connect to CLI via Telnet	177

Command Groups	184

# Overview

#### CONFIGURATION VIA WEB CONSOLE

- Open the web browser. We recommend using "Google Chrome".

Note: If the web browser is not supported, the warning message will be showed up.

- Enter the IP Address in the URL field to connect to the switch and click "Enter" key.

Note: The default IP Address is "192.168.10.1". The Login Page is displayed.

- Enter the Username and Password and click "Login" Button to login to the system.

Note: The default Username and Password is admin / admin.

After logging into the system, the "Overview" page is displayed.

#### GLOBAL FUNCTIONS

Five global functions are provided in the header field.

1.     Hide/Show Model Information

When a low-resolution environment is used to configure the system via the web console, the "Model Information" field can be hidden to have a better view.

Show Model Information:

Hide Model Information:

2.     Save Configuration

After configuring, click the icon to save the configurations to the "startup-config" file. The configurations are retained in the system until a factory reset default is done.

3.     Restore Factory Default

Removes the configurations saved in the system. After restoring factory default, all the settings will be set to default values.

4.    Reboot System

Reboots the device and restarts the system.

5.    System Logout

This option enables you to sign out from the system. Users have to login again if they want to configure the settings.

The system will auto-logout after the "timeout" timer expires. The "timeout" timer is configured in the CLI mode by using the "exec-timeout" command.

The maximum value of the timer in the web console is 30 mins.

6.    Change Language

We support multi-language from firmware version 1.1.72. The default language is English and

Traditional Chinese is also supported by default. If you need other languages, please contact us.

A USER-FRIENDLY DATA TABLE

A user-friendly data table is provided on the “IPv6 Neighbor Table”, “IGMP Snooping Table”, “VLAN Table”, “LLDP Neighbor Table”, and “MAC Address Table”. The following section details how to use the data table functions to help the users to observe the information easily.

The following example is “MAC Address Table”.



Users will be able to select a value to display the number of entries in one page. The following values can be selected - “10”, “25”, “50”, and “100” selections. By default, “10” is selected.



The search option enables you to search a key word in the data. It will search all the columns and identify the data rows that match the search criteria.



It displays the total number of entries and the current entry number.

  - and

This option orders the field from smaller to larger or from larger to smaller.



Changes to “First”, “Previous”, “Next”, or “Last” page.

In addition to the above functions, “Refresh” and “Auto Refresh” function are available for all status page including “IPv6 Neighbor Table”, “RSTP Port Status”, “DHCP Leased Table”, “Port Status”, “IGMP Snooping Table”, “VLAN Table”, “Trunking Status”, “LLDP Neighbor Table”, and “MAC Address Table”.



Selecting this checkbox enables the “Auto Refresh” function and deselecting the checkbox disables the “Auto Refresh” function.



The Refresh Rate option is a global configurable variable. When the Auto Refresh option is enabled, the status will refresh automatically based on the Refresh Rate interval.

The range of the Refresh Rate is from 5 to 300 second(s). The default Refresh Rate is 5 seconds.

  - (Refresh Button)

You can click the “Refresh” button to manually refresh the status.

# System Information

#### CONFIGURE SYSTEM INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Host Name

It is useful to identify the difference between the switches, for example: CoreSwitch01. The max. length for the Host Name is 32 characters.

Note: #, \, ', ", ? are invalid characters.

##### System Description

The System Description is default defined by the system.

It contains the copper port number, fiber port number, and PoE information (if supported). The max. length for the System Description is 68 characters.

Note: #, \, ', ", ? are invalid characters.

##### Switch Location

It is useful to find the location of the switches, for example: Area01. The max. length for the Switch Location is 32 characters.

Note: #, \, ', ", ? are invalid characters.

##### Contact Information

Records the information of the person responsible for this device and the contact details.

Note: #, \, ', ", ? are invalid characters.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# IPv4 (VLAN IP)

Internet Protocol Version 4 (IPv4) is the fourth version of the Internet Protocol. It is used on the packet-switched networks and with connectionless communication. IPv4 has four bytes (32 bits) address, and the address space is limited to 4,294,967,296 (232) unique addresses. On the local area network (LAN), the “Private Network” is used. It starts from 192.168.0.0 and the address space contains 65,025 (216) IP addresses. The frames can only be sent to the host in the same subnet. For example, the default IP Address of the switch is “192.168.10.1”. When the users want to connect to the web console of the switch, an IP address from “192.168.10.2” to “192.168.10.254” must be assigned to the host.

We usually configure VLANs to divide broadcast domains in the Local Area Network (LAN). To communicate with others in another VLAN, we need the device to support inter-VLAN routing. Users can use VLANs to create Layer 3 interfaces by assigning IP address in different subnets to the VLAN. Before configuring any kind of routing protocols, users must make sure the VLAN IP Address is configured.

The Loopback Interface is a virtual interface for management or identity. It is more stable than physical interface and never goes down when physical interface fails. However, currently there are some limitations in our switches.

    - Loopback Interface is only supported on the IPv4

    - Only support one Loopback Interface

    - The IP Address of Loopback must be different from the IP Addresses of Interfaces (VLANs).

CONFIGURE IPV4 INFORMATION

##### DNS Server 1 / 2

Specifies the IP address of the DNS Server so that the users can connect to another device based on the URL instead of the IP address.

The default DNS Server 1 is "8.8.8.8". It is provided by Google. The default DNS Server 2 is BLANK.

##### Loopback Settings

- IP Address

Assign a unique static IP Address for Loopback Interface.

Note: the IP Address of Loopback must be different from the IP Addresses of Interfaces (VLANs).

- Subnet Mask

Define the type of network of Loopback Interface.

##### Interface Settings

- VLAN ID

Users must create VLAN in the VLAN Settings Page before configuring its IP Address.

- IP Address

Assign a unique static IP Address for the VLAN ID. The default IP Address for VLAN 1 is "192.168.10.1".

- Subnet Mask

Define the type of network, to which this device is connected to. The default Subnet Mask for VLAN 1 is "255.255.255.0".

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# IPv6 (VLAN IP)

Internet Protocol Version 6 (IPv6) is a solution to deal with the address space limitation of IPv4 and it is the most recent version of Internet Protocol. It is intended to replace IPv4. IPv6 is a Layer 3 (Internet Layer) protocol, which is used on the packet-switched networks and with connectionless communication. There are 16 bytes (128 bits) for an IPv6 address, and the address space is up to 2128 unique addresses. The IPv6 address is usually represented in hexadecimal digits, 8 groups of 4 digits, and each group is separated by a “:” (colon). For example, the DNS server address in IPv6 is “2001:4860:4860:0000:0000:0000:0000:8888”.

CONFIGURE IPV6 INFORMATION

For more information, hover the mouse over the	icon in the system.

##### VLAN ID

Users must create VLAN in the VLAN Settings Page before configuring its IP Address.

##### IPv6 Addresses

Enables the users to define an IPv6 addresses for each created VLAN.

The IPv6 address contains 2 section - IPv6 address and prefix. The default Prefix is 64-bit. : Click the remove icon to delete the IPv6 Address row.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# System Time

The System Time represents the date and time. The system uptime defines the passing time after the system boots up. There is no battery on the switch and hence the system time cannot be saved in the system. Users can configure the time zone and system time manually by synchronizing the time with the browser or by enabling the “NTP” service to get the time from a NTP Server.

## NTP

Network Time Protocol (NTP) is a clock synchronization protocol, which is used to synchronize the system time with the NTP server. NTP is one of the oldest Internet Protocols in use from 1985 until now. It works based on a client-server model, but it can also be used in peer-to-peer relationships. The NTP application on the switch is follows the client-server model and the switch plays a role in the NTP Client.

#### CONFIGURE SYSTEM TIME INFORMATION

##### System Time Information

- Current Time: The current date time of the system.

Note: Time format: Year/Month/Day 24HR:Min:Sec.NanoSec

- System Uptime: The system boot up duration.

##### NTP Settings

- NTP Mode

"Enable" or "Disable" NTP Service. If NTP Mode is enabled, the system will sync time with NTP Server on an hourly basis.

- NTP Server 1 & 2

This field displays the URL or the IP address of the host that provides the NTP Service. There are 2 server configurations supported.

##### Manual Time Settings

- Time Zone

Select the Time Zone to define the local time offset from GMT.

- Date Selector

Select the system date manually. The format is "year/month/day".

- Time Setting

Define the system time manually. The format is "hour:minute:second".

- Sync with Browser

Select the checkbox to synchronize the system time with the browser time.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Precision Time Protocol (PTP)

| The Precision Time Protocol (PTP) is used to synchronize clocks and it is more accurate than NTP. PTP is majorly employed to synchronize the network devices that require precise timing like financial transactions. Synchronization and management of a PTP network is implemented by the exchange of messages across the communications devices. PTP is working by a Master and Slave structure. There are three types of PTP clocks – Ordinary Clock, Boundary Clock, and Transparent Clock and currently we support Ordinary Clock and Transparent Clock on the L2, Router, and L3 switches, and Boundary Clock on the Router and L3 switches. If the switch is an Ordinary Clock, it can be configured as role Master or Slave. For the Boundary Clock and Transparent Clock, they can be both Master and Salve at the same time to synchronize with the Master and forward to Salves. |  |
| --- | --- |

CONFIGURE PTP BASIC INFORMATION – ORDINARY CLOCK

For more information, hover the mouse over the	icon in the system.

##### PTP Status

"Enable" or "Disable" the PTP protocol.

Note: The PTP Slave and NTP Client are mutually incompatible, if users want to enable PTP mode with role Slave, please make sure the NTP Client is disabled.

##### PTP Mode

There are 3 roles of PTP that supported on the switch – Master, Slave, and Boundary Clock. The advanced settings of these modes are different, and the configurations are presented on the Configure PTP OC Master, Configure PTP OC Slave, and Configure PTP Boundary Clock sections.

##### Domain ID

The ID is the identifier of the PTP network. Only the nodes with the same Domain ID synchronize the time in the network.

The default value of Domain ID is 0

The range of Domain ID is from 0 to 127

##### Interface1

This field is to assign an interface for PTP function. It is the Master interface when PTP is running on Boundary Clock mode.

The default value of Interface1 is 1

The range of Interface1 is from 1 to 4094

##### Interface2

The field Interface2 is only supported on Boundary Clock mode. It is the Salve interface of Boundary Clock.

The default value of Interface2 is 0

The range of Interface2 is from 1 to 4094

CONFIGURE PTP ADVANCED SETTINGS

For more information, hover the mouse over the	icon in the system.

##### Priority 1

The Priority is used to decide the Best Master when there are several Master nodes in the PTP network. If there are 2 or more Masters with the same Priority 1, the system will refer to the Priority 2.

The default value of Priority 1 is 128

The range of Priority 1 is from 0 to 248

Note: the lower the value the higher the priority

##### Priority 2

The Priority is used to decide the Best Master when there are several Master nodes with the same Priority 1 in the PTP network. If there are 2 or more Masters with the same Priority 2, the system will refer to the Clock Identity (MAC Address).

The default value of Priority 1 is 128

The range of Priority 1 is from 0 to 248

Note: the lower the value the higher the priority

##### Announce Interval

The Announce Interval is the period to send Announce Message.

The range of Announce Interval is from -1 to 7

##### Announce Timeout

The Announce Timeout is the timer for announcing timeout message.

The default value of Announce Timeout is 6

The range of Announce Timeout is from 2 to 255

  - Sync Interval

The Sync Interval is the period to send Sync Message.

The range of Sync Interval is from -7 to 7

The mapping for Announce Interval and Sync Interval to second(s) is as following table:

| Interval | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Seconds | 1s | 2s | 4s | 8s | 16s | 32s | 64s | 128s |
| Interval |  | -1 | -2 | -3 | -4 | -5 | -6 | -7 |
| Seconds |  | 512ms | 256ms | 128ms | 64ms | 32ms | 16ms | 8ms |

##### Period

The Period is a timeout period. The Slave node will wait n (Period Value) times that announce receipt timeout before resetting.

The default value of Period is 0

The range of Period is from 0 to 20

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

PTP STATUS – MASTER

##### PTP Device Type

This field is the type/role of switch that in a PTP network. The switch can be “Master Only”

or “Slave Only” currently because we only support Ordinary Clock now.

##### Clock Domain

This field shows the Domain ID that the system is in now.

##### Clock ID

This field is the identity of the switch in the PTP network. The Clock Identity is configured to the MAC Address of the switch by default.

##### Best Master ID

The Best Master ID is the Clock Identity of the Best Master in a PTP network. If there are several Master in the PTP network, users can understand which one is the Best Master through this field.

##### Priority 1

This field is the value of Priority 1 that is configured.

##### Priority 2

This field is the value of Priority 2 that is configured.

##### Class

The Class field is usually named colckClass. The values of PTP clock classes are based on the traditional quality levels from SSM/ESMC.

PTP STATUS – SLAVE

##### PTP Device Type

This field is the type/role of switch that in a PTP network. The switch can be “Master Only”

or “Slave Only” currently because we only support Ordinary Clock now.

##### Clock Domain

This field shows the Domain ID that the system is in now.

##### Clock ID

This field is the identity of the switch in the PTP network. The Clock Identity is configured to the MAC Address of the switch by default.

CONFIGURE PTP BASIC INFORMATION – TRANSPARENT CLOCK

Known Limitations:

The Transparent Clock is only supported on the following conditions:

- VLAN untagged mode

- L2 management switches

- Copper ports and 1G SFP Slots

- One-step Mode

- End-to-End delay mechanism

  - Port

Port 1 to Port N, where N is based on the total port number.

##### Mode

Select Transparent Mode or Normal Mode (None) on the designated port.

##### Status

“Enable” or “Disable” selected mode on the designated port.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Spanning Tree

The Spanning-Tree Protocol is a standard protocol that is defined in IEEE 802.1D. It is used to build a logical loop-free topology for layer-2 Networks. The basic function of the protocol is to prevent loops and broadcast flooding around the switches. STP allows spare links in the network design to provide backup paths when the active link fails and requires a convergence time of 30-50 seconds to recover the topology when the topology is changed. This prompted the use of Rapid Spanning-Tree Protocol as it provides a faster convergence when the topology is changed.

RSTP was introduced by IEEE as 802.1w. It can respond within 3 x "Hello Time" when a topology is changed. The "Hello Time" is a configurable value, and it is important for RSTP. The default RSTP value is 2 seconds and typically, the convergence time for RSTP is under 6 seconds. RSTP is much faster than STP. RSTP should be used instead of STP.

The Multiple Spanning-Tree Protocol defined in the IEEE 802.1s is an extension to RSTP for Virtual LANs. MSTP provides a better alternate path than STP/RSTP for different VLANs. It can make a group of VLANs more systemized in the topology.

CONFIGURE RSTP/CIST BASIC INFORMATION

For more information, hover the mouse over the	icon in the system.

##### System Time Information

RSTP: Enable STP and run "RSTP" for redundancy.

MSTP: Enable STP and run "MSTP" for redundancy.

Disable: Disable STP. Users must enable another protocol to prevent from loop.

##### Root Priority

It is used to define the "Root Bridge". The bridge with the lowest Root Priority is the "Root Bridge". If all the bridges are set to the same Root Priority value, the system will select the Root Bridge based on the MAC Addresses.

The range of Root Priority is from 0 to 61440 (multiple of 4096). The default Root Priority is 32768.

##### Hello Time

It is particularly important and used to determine the interval to send BPDU (management frame) to check the RSTP topology and status.

The range of Hello Time is from 1 to 10 second(s). The default Hello Time is 2 seconds.

##### Forward Delay

A delay/timer is used to determine when to change the Path State from Learning/Listening to Forwarding.

The range of Forward Delay is from 4 to 30 seconds. The default Forward Delay is 15 seconds.

##### Maximum Age

A timer that is used to wait for the Hello BPDU from the Root Bridge. If this device receives the BPDU before the timer expires, the timer will be reset. Else, the device will send the topology changed BPDU to notify other devices.

The range of Maximum Age is from 6 to 40 seconds. The default Maximum Age is 20 seconds

The relationship between "Hello Time", "Forward Delay", and "Maximum Age" is:

2 x (Forward Delay - 1 sec) >= Max Age >= 2 x (Hello Time + 1 sec)

CONFIGURE RSTP PORT INFORMATION

##### Port

For more information, hover the mouse over the	icon in the system.

Port 1 to Port N, where N is based on the total port number.

##### Path Cost

The cost from the current node to another device. The range of Path Cost is from 0 to 200000000.

The default Path Cost is 0. This implies that the Path Cost is decided by the system.

##### Port Priority

Used to decide the port to be blocked in the Ring topology.

The range of Root Priority is from 0 to 240 and are in multiple of 16. The default Root Priority is 128.

##### Admin P2P

The Admin P2P is the link-type for each port.

P2P: It is a full-duplex link.

Shared: It is a half-duplex link.

##### Edge

A port that can connect to a non-STP device is called an Edge port. Users can manually fix a port to non-Edge or Edge.

Auto: The system automatically identifies an Edge or Non-Edge.

Edge: The port is forced to be an Edge port. An edge port will directly be transitioned to the "Forwarding" state and is not required to wait for the "Forward Delay". If a port is directly connected to a non-STP device, users can manually set it to "Edge" and enable it to transmit faster.

Non-Edge: The port is forced to be a Non-Edge port. This implies that the port will go through Learning/Listening to Forwarding state even though it is connected to an end device or not.

##### Admin STP

"Enable" or "Disable" the Spanning-tree protocol that is running on the specific port.

           (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

RSTP/CIST STATUS

##### Bridge ID

This field shows the unique identity of this node when it is part of a network. It contains 8 bytes - the first 2 bytes are for Bridge Priority (configurable) and the remaining 6 bytes are for the MAC Address (unique).

##### Root Bridge

It is elected from the switches in the STP topology via several STP messages (BPDU). The Root Bridge is the node with the lowest Root Priority. If all the nodes are with the same Root Priority, the Root Bridge will be selected based on their MAC Addresses.

##### Root Priority

It is used to define the "Root Bridge". The bridge with the lowest Root Priority is the "Root Bridge". If all bridges are set to the same Root Priority value, the system will select the Root Bridge based on the MAC Addresses.

##### Root Port

It is the port that is connected to the Root Bridge and with the lowest cost. If the Root Port shows "none", it implies this node is the Root Bridge.

##### Root Path Cost

It is the cost from the current node to the Root Bridge.

##### Hello Time

It is used to determine the interval to send BPDU (management frame) to check the RSTP topology and status.

##### Forward Delay

It is used to determine when to change the Path State from Learning/Listening to Forwarding.

##### Max Age

It is used during waiting for Hello BPDU from the Root Bridge.

##### Port

Port 1 to Port N, N is based on the total port number.

##### Role

This field shows the role of the STP port.

Root: This is the root port, which is connected to the Root Bridge with the lowest cost.

Designated: This is the designated port, which can send the best BPDU on the segment to other connected nodes.

Alternate: This is the alternate port, which is blocked. This port can still receive useful BPDU from another bridge. When it receives a useful BPDU, it will help to forward it on the segment.

Backup: This is the backup port, which is blocked. It corresponds with “Alternate Port” to the blocking state. This port also receives useful BPDU, but the BPDU is from the same bridge. When it receives a useful BPDU, it will help to forward it on the segment.

Disabled: The port is not linked up.

##### Path State

This field shows the path state of this STP port.

Discarding: The port state can be “Disabled”, “Blocking”, or “Listening”. The incoming frames are dropped and learning MAC addresses are stopped.

Learning: The port is learning MAC addresses, but the incoming frames are dropped.

Forwarding: The port in the forwarding state forwards the incoming frames based on the learned MAC address table.

##### Port Cost

This is the cost from the port to the Root Bridge. Spanning-tree Protocol assumes the path cost is determined by the access speeds of the links. The default RSTP path cost is shown in the following table:

| Speed | RSTP Path Cost | Speed | RSTP Path Cost |
| --- | --- | --- | --- |
| 4 Mbps | 5,000,000 | 1000 Mbps (1Gbps) | 20,000 |
| 10 Mbps | 2,000,000 | 2000 Mbps (2 Gbps) | 10,000 |
| 16 Mbps | 1,250,000 | 10000 Mbps (10 Gbps) | 2,000 |
| 100 Mbps | 200,000 |  |  |

##### Port Priority

The Port Priority is used to determine the Root Port on a non-root bridge. The port with the lowest Port Priority value gets the higher priority.

##### Oper. P2P

This field shows the link-type of the STP port. P2P means “point-to-point” and Shared means “point-to-multiple”.

##### Oper. Edge

This field shows the edge state of this STP port.

CONFIGURE MSTI INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Basic Settings

- Region Name

The Region Name is the name of the MST Region. The switches in the same MST Region must be set to the same Region Name.

The max. length for the Region Name is 32 characters. Note: #, \, ', ", ? are invalid characters.

- Revision Number

The Revision Number is the level of the MST Revision. The switches in the same MST Region must be set to the same Revision Number.

The range of the Revision Number is from 0 to 65535.

The default Revision Number is 0.

##### Instance Settings

- Instance

The Instance is from 1 to 15.

- Included VLAN

The configured VLANs are involved in the specific Instance.

The format is: 10, 20, 30…. “Comma” is used to separate VLAN IDs.

- Priority

The priority is used to define the “Root Bridge” that is used to communicate with other MSTI Region.

The range of the Root Priority is from 0 to 61440 (multiple of 4096). The default Root Priority is 32768.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE MSTI PORT INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Instance Selector

Select the instance to configure the ports. The Instance No. is from 1 to 15.

##### Port

Port1 to PortN, where N is based on the total port number.

##### Path Cost

The Path Cost is the cost from the current node to another device. The range of the Path Cost is from 0 to 200000000.

The default Path Cost is 0. This implies that the Path Cost is decided by the system.

##### Port Priority

This is used to identify the port to be blocked in the Ring topology.

The range of the Root Priority is from 0 to 240 and is in multiples of 16. The default Root Priority is 128.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# ERPS

Ethernet Ring Protection Switching (ERPS) applies the protection switching mechanism for Ethernet traffic in a ring topology. This mechanism is defined in ITU-T G8032. You can have a protection switching and avoid the possible loops in a network by implementing the ERPS function. This is done by blocking the flow of traffic to the Ring Protection Link (RPL) there by protecting the entire Ethernet ring.

When an ERPS is implemented in a ring topology, only one switch is allocated as the owner. This switch oversees blocking the traffic in the RPL to avoid loops. The switch adjacent to the RPL owner is called the RPL neighbor node and it is responsible for blocking the end of the RPL during normal condition. The participating switches that are adjacent to the RPL owner or neighbor in a ring are called the members or RPL next-neighbor nodes. The primary function of these switches is to forward the received traffic.

The benefit of the ERPS ring protection switching architecture are:

- Protection switching on Ethernet layer

- Preventing loop by blocking mechanism

- VLAN based protection

- Sub-50msec protection switching

- Support administration command

- 250 switches and links in singled ring tested

To make sure that a ring is up and loop-free, Ring Automatic Protection Switching message is sent regularly as control messages by nodes on the ring. The RPL owner identifies a signal failure (SF) in a ring when the RPL owner misses the poll packets or reads from the fault detection packets. When the fault is identified, the RPL owner unblocks the ring protection link (RPL) and permits the protected VLAN traffic through.

ERPS, like STP, provides a loop-free network by using polling packets to detect faults. If a fault occurs, ERPS restores itself by sending traffic over a protected reverse path rather than making a calculation to identify the forwarding path. The fault detection mechanism in the ERPS enables the ERPS to join in less than 50 milliseconds and recovers quickly to forward traffic. In a real test case, the protection switching time is 15ms in 250 devices single ring topology.

In the new ERPS version, G.8032 v2, it supports multiple ring or ladder topology. Rings can conjoin by one or more interconnection nodes. The major ring controls a full physical ring. Sub ring does not constitute a closed ring. It is connected to a major ring at the interconnection nodes.

Using major ring and sub ring can design multiple ring or ladder topology. With these topologies, ERPS can append to variance application with different level of ring network. For example, core ring and branch ring architecture has application in campus and the area with central control node. Ladder topology has lots of case for tunnel and train application. The benefit of small ring is less effect nodes if ring caused of recovery.

CONFIGURE ERPS INFORMATION

For more information, hover the mouse over the	icon in the system.

##### ERPS Ring

There are three rings supported on a device. Using the dropdown select to change the ERPS Rings.

##### Basic Settings

- ERPS Status

“Enable” or “Disable” ERPS protocol running on the switch. By default, the ERPS protocol is disabled.

- Ring Type

Major-ring: controls a full physical ring.

Sub-ring: connected to another ring. It does not constitute a closed ring.

- ERPS Port 0

The ERPS Port 0 is also called “West Port”. Select one of the switch ports to be the Port 0 of ERPS and decide the role of the port.

- ERPS Port 1

The ERPS Port 1 is also called “East Port”. Select one of the switch ports to be the Port 1 of ERPS and decide the role of the port.

Note: Only One of the switch ports can be configured as ERPS Port 0 or ERPS Port 1.

| Role | Description |
| --- | --- |
| Owner | There is only one “Owner” in the ERPS ring topology. The Owner is responsible for blocking the traffic in RPL and protects one side of the RPL. |
| Neighbor | There is only one “Neighbor” in the ERPS ring topology. The Neighbor is the port connected with the Owner port and protects another side of the RPL. |
| Interconnection | The Interconnection port connects a major-ring and a sub-ring. If one of the ports on the switch is set to “Interconnection” role, the other port will be set to “Disabled” automatically. |
| None | The “None” implies that the port is other than an Owner or a Neighbor. |

- ERPS Ring ID

The ID is the identifier of the ring. The members in the same ring must be set to the same ERPS Ring ID.

The range of the ERPS Ring ID is from 1 to 239.

The default ERPS Ring ID is 1.

。 R-APS Channel

The R-APS Channel is used to forward ERPS information and is mapped to the VLAN IDs. These VLAN IDs cannot be set as traffic VLAN ID. The members in the same ring must be set to the same R-APS Channel.

The range of the R-APS Channel is from 1 to 4094.

The default R-APS Channel is 1000.

##### Advanced Settings

The Advanced Settings field is only displayed when the “Advanced Settings” checkbox is selected in the Basic Settings.

- Major-Ring Virtual Channel

This field is used to configure the specific virtual channel for transmitting the management packets of the sub-ring through the major-ring.

- Sub-Ring Virtual Channel

“Enable” or “Disable” using virtual channel in the sub-ring. When the Sub-Ring Virtual Channel is enabled, ERPS protocol will transmit management packets by the configured virtual channel.

- Revertive Mode

“Enable” or “Disable” the ERPS Revertive Mode. If the Revertive Mode is enabled, the blocked link will revert to the RPL link after the failed link is recovered.

By default, the ERPS Revertive Mode is enabled.

- MEL Value

MEL field is for the compliance with other devices which are running ITU-T G.8031 from third-party. The MEL implies the MEG Level. It is a field in the R-APS PDU. A large MEL value involves more devices. For example, level 7 contains levels 0 to 6.

The range of the MEL Value is from 0 to 7.

The default MEL Value is 7.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

ERPS STATUS

##### ERPS Ring

There are three rings supported on a device. Using the dropdown select to change the ERPS Rings.

##### Basic Information

- Ring Type

The type of the selected ERPS Ring shows “Major-ring”, “Sub-ring with virtual channel”, or “Sub-ring without virtual channel”.

- ERPS Status

The status of ERPS is “Enable” or “Disable” in the selected ERPS Ring.

- Ring State

There are two states for ERPS Rings: Normal and Abnormal.

- Node State

There are three states for ERPS Nodes: Initial, Idle, Pending, and Protection.

| State | Description |
| --- | --- |
| Initial | The ERPS protocol is disabled in the selected ring. |
| Idle | The ERPS protocol is enabled in the selected ring and the ERPS ring is under control by the RPL Owner. |
| Pending | The ERPS protocol is enabled in the selected ring. The ERPS ring is recovery from Protection state and is waiting for the wtr timer expired. |
| Protection | The ERPS protocol is enabled in the selected ring but one of the links in the ring is broken. The RPL changes to forward to keep the ring working. |

- ERPS Ring ID

The ID is the identity for the selected ERPS Ring.

- R-APS Channel

This field shows the configured R-APS Channel.

- Virtual Channel

This field shows the virtual channel of sub-ring. If the field shows “default” implies the virtual channel follows the R-APS Channel.

- Revertive Mode

Show the Revertive Mode is enabled (Yes) or disabled (No).

- MEL Value

The field is the configured MEL value.

##### Port Status

- Interface

The configured port presents the ERPS port 0/1 in the ERPS protocol.

- Role

Display the configured role for the configured port.

# MRP

MRP function is only supported on the CP-0804X

Media Redundancy Protocol (MRP) is an IEC standard protocol to prevent the ring topology from loop, and it is defined as IEC 62439-2. The recovery time of MRP is much faster than STP and even than RSTP, so it is suitable in most Industrial Ethernet applications.

In the ring topology with MRP, the manager is called Media Redundancy Manager (MRM),  and the clients are called Media Redundancy Clients (MRC). The MRM send test packets from both of its ring ports periodically to confirm the health of ring topology.

There are three states for MRP Ring Ports – Disabled, Blocked, and Forwarding. When the  MRP ring is under normal operation, the network works in the Ring-Closed state. In the closed state, one of the MRM Ring Ports is blocked and the other one is forwarding, while both ring ports of MRCs are forwarding. Due to the blocked port, the topology is a logical stub, and the loops are avoided. If one of the forwarding links is failed, the ring topology goes to open state, and the blocked port of MRM will be forwarding state to insure the transmission in the ring.

| Ring Topology Closed | Ring Topology Open |
| --- | --- |

If the MRC detects a link down at one of the ring ports, it can notify this event to the MRM initiatively. In Advanced Mode, the MRM can activate the blocked ring port to speed-up recovery rather than wait till sufficient loss of test packets.

MRP standard guarantees the recovery time in the specifications. The recovery time are 500ms, 200ms, 30ms with maximum 50 switches, and 10ms with up to 14 switches in a ring. Currently, we support the recovery delay of 500ms and 200ms.

CONFIGURE MRP INFORMATION

For more information, hover the mouse over the	icon in the system.

##### MRP Status

“Enable” or “Disable” MRP protocol running on the switch. By default, the MRP protocol is

disabled.

  - MRP Role

Configure the role of the switch when running MRP protocol. The “Manager” item implies MRM, and the “Client” item implies MRC.

##### MRP Recovery Delay

The MRP Recovery Delay implies to the number of lost packets. The IEC 62439-2 standard defines 4 recovery delays – 500ms, 200ms, 30ms, and 10ms. Currently, we only support 500ms and 200ms.

##### MRP Port 1 (Primary)

The MRP Port 1 is the primary port of MRP. Select one of the switch ports to be the primary port of MRP. The Primary port is default configured to be forwarding when the Ring is closed.

##### MRP Port 2 (Second)

The MRP Port 2 is the secondary port of MRP. Select one of the switch ports to be the secondary port of MRP. The secondary port is default configured to be blocking when the Ring is closed.

##### MRP Domain Name

The MRP Domain Name is a unique string for the MRP domain to identify MRP domains

##### MRP Domain ID

The MRP Domain ID is the key attribute to define the members in the same MRP ring. The default MRP Domain ID is

255.255.255.255.255.255.255.255.255.255.255.255.255.255.255.255.

  - Advanced Mode

The Advanced Mode is supported only when the MRP Role is configured to “Manager”. If the Advanced Mode is checked, it implies the Advanced Mode is enabled. Under the advanced mode, when the MRM received a link-down signal, the MRM actives the backup port immediately rather than waiting for the sufficient loss of test packets.

MRP STATUS – BASIC & CONFIGURE INFORMATION

##### Basic Information

- Instance ID

The Instance ID is the Ring ID. We only support one ring currently, so the Instance ID displays always 1.

- Domain ID

The Domain ID is the identity of current MRP ring. Only the members with the same Domain ID will be regarded as working in the same ring.

##### Configured Information

- Advanced Mode

The field shows the status of Advanced Mode. Advanced Mode is only supported when the switch is configured as an MRM (Manager).

- Role of Switch

There are 2 roles of switches in the MRP – Manager and Client Administrative Setting: the role that users configured for the switch. Real Operating State: the role that the switch is working as.

- Domain Name

This field shows the configured name of this MRP Domain.

- Recovery Delay

This field shows current operating Recovery Delay. It may be 500 or 200 (msec).

- Port Number, Secondary

- Port Number, Primary

These two fields shows two parts of information. The first one is the switch port number configured as Primary / Secondary Port, and the other one is the state of this port. There are 3 states for MRP ports when the MRP is enabled: Forwarding, Blocked, and Disabled. If the MRP is disabled, the state shows “N/A”.

- Operation

This field shows current Operation State – Enabled or Disabled.

##### Operating States (Master)

。 Ring State

The Ring State displays the actual ring sate of MRP, and the state may be

Open: some of the links in the MRP ring are down or MRC failure.

Closed: the MRP ring is closed and under normal operation without error.

- Topology Change Interval

The interval is the period to send MRP_TopologyChange frames.

- Topology Change Repeat Count

The count is the repeat times to transmit MRP_TopologyChange frames.

- Short Test Interval

This interval is a timer used after link changes to send MRP_Test frames on the MRP ring ports.

- Default Test Interval

The interval is the default period to send MRP_Test frames on the MRP ring ports.

- Test Monitoring Count

This field is the interval count for monitoring the reception of MRP_Test frames.

- Non-blocking Client Supported

This field displays the ability of the MRM to support MRCs without BLOCKED port state support in the ring.

- Test Monitoring Extended Count

This field is an optional parameter. It is an extended interval count for monitoring

the reception of MRP_Test frames.

- Check Media Redundancy

Check the current state of MRM. The state may be “Enabled” or “Disabled”.

##### Operating States (Client)

- Link Down Interval

The Link-down Interval shows the period that MRP Link-down frames sent on the ring port. The default value of Link-down Interval is 20ms.

- Link Up Interval

The Link-up Interval shows the period that MRP Link-up frames sent on the ring port. The default value of Link-up Interval is 20ms.

- Link Change Count

The Link-change Count controls the repeated times to transmit MRP Link-Change frames. The default Link-change Count is 4 times.

- Blocked Support

The Blocked Support is default enabled. The MRM with Blocked Support will block the secondary port when there is no Blocked Port in the MRM ring topology to avoid loops.

# SNMP

Simple Network Management Protocol (SNMP) is a standard for collecting and structuring information on the managed devices of the IP network. It can also modify some of the information to change the behavior of the devices. SNMP is usually used in monitoring the network. The users can remotely query the information provided by the devices running SNMP.

The switches support SNMP v1, v2c, and v3. SNMP v1 and v2c authenticates with a community string for “read-only” or “read-write” permission. The SNMP v3 authentication requires to select an authentication level (MD5 or SHA) and supports data encryption to make the data safer.

For the SNMP version and authentication method relationship, refer to the table below:

| Version | Web Setting | Authentication | Encryption | Method |
| --- | --- | --- | --- | --- |
| v1 & v2c | Read Only Community | Community String | No | String match for authentication |
|  | Read-Write Community | Community String | No | String match for authentication |
| v3 | Security Level – No Authentication, No Privacy | No | No | Access by an account (admin or user) |
|  | Security Level – Authentication, No Privacy | MD5 / SHA | No | Access by an account (admin or user) and password with more than 8 characters, which is based on MD5 or SHA |
|  | Security Level – Authentication, Privacy | MD5 / SHA | Yes AES / DES | Access by an account (admin or user) and password more than 8 characters, which is based on MD5 or SHA. The data encryption is based on AES or DES and the key requires 8 to 32 characters. |

CONFIGURE SNMP SERVER INFORMATION

For more information, hover the mouse over the icon in the system.

##### Basic Settings

- SNMP Version

The system enables the SNMP “v1, v2c and v3” authentication by default. The users can enable the SNMP server on only “v1 and v2c” or “v3”. “None” refers to disabling the SNMP server.

- Read Only Community

The community used to access the SNMP server with the “read-only” privilege.

The max. length for the Read Only Community is 32 characters. Note: #, \, ', ", ? are invalid characters.

- Read-Write Community

The community used to access the SNMP server with the “read-write” privilege.

The max. length for the Read-Write Community is 32 characters. Note: #, \, ', ", ? are invalid characters.

##### SNMPv3 Settings

This section is displayed only when the SNMP Version is set to “v3” or “v1, v2c and v3”. Two accounts are provided – Admin and User to access the SNMP agent. The users can set different levels for the 2 accounts.

- Security Level

No Authentication, No Privacy: Access by an account “admin” or “user”.

Authentication, No Privacy: Access by an account “admin” or “user” with password. Authentication, Privacy: Access by an account “admin” or “user” with password and the data will be encrypted.

- Authentication Type

Two algorithms are provided - MD5 and SHA for authentication password.

- Authentication Password

A string/key is used to authenticate the SNMP Server and obtain the access permission. It will be hashed by MD5 or SHA before authentication.

The min. length for the Read-Write Community is 8 characters. The max. length for the Read-Write Community is 32 characters. Note: Only digits, letters and underline are valid.

- Encryption Type

Two algorithms are provided - AES and DES for data encryption.

- Encryption Password

A string/key is used to encrypt the data that is sent to the SNMP server.

The min. length for the Read-Write Community is 8 characters. The max. length for the Read-Write Community is 32 characters. Note: Only digits, letters and underline are valid.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE SNMP TRAP INFORMATION

For more information, hover the mouse over the icon in the system.

##### Basic Settings

- Trap Mode

The system enables the SNMP “v1, v2c and v3” authentication by default. Users can enable the SNMP server only on “v1 and v2c” or “v3”. “None” indicates disabling the SNMP server.

- Inform Retry

The SNMP trap will send “Retry” times when the trap set to “v2 Inform” or “v3 Inform” mode.

The range of the Inform Retry is from 1 to 100. The default Inform Retry is 5.

- Inform Timeout

The interval is used to send trap when the trap set to “v2 Inform” or “v3 Inform” mode.

The range of the Inform Retry is from 1 to 300 second(s).

The default Inform Retry is 1 second.

- Trap Receiver IP 1 & 2

The IP address is the IP address of the trap server to receive the trap information. The system supports both IPv4 and IPv6 addresses for the receiver. There are 2 Trap Receiver IP supported.

- Community

The string in the SNMP trap is the identity of the device.

The max. length for the Community is 32 characters. Note: #, \, ', ", ? are invalid characters.

##### SNMPv3 Trap/Inform Settings

This section is displayed only when Trap Mode are set to “v3 Trap” or “v3 Inform”.

- Username

Specify the username for authentication with the SNMP trap server.

- Engine ID

The Engine ID is the identifier for the given SNMP application.

- Security Level

No Authentication, No Privacy: Access using the username assigned to the users.

Authentication, No Privacy: Access using the username assigned to the users with password.

Authentication, Privacy: Access using the username assigned to the users with password and the data will be encrypted.

- Authentication Type

Two algorithms are provided - MD5 and SHA for authentication password.

- Authentication Password

A string/key is used to authenticate the SNMP trap server and obtain the permission. It will be hashed by MD5 or SHA before authentication.

The min. length for the Read-Write Community is 8 characters. The max. length for the Read-Write Community is 32 characters. Note: #, \, ', ", ? are invalid characters.

- Encryption Type

Two algorithms are provided - AES and DES for data encryption.

- Encryption Password

A string/key is used to encrypt the data sent to the SNMP trap server.

The min. length for the Read-Write Community is 8 characters. The max. length for the Read-Write Community is 32 characters. Note: #, \, ', ", ? are invalid characters.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# DHCP

DHCP SERVER/CLIENT

DHCP, Dynamic Host Configuration Protocol, is a standardized protocol used in the IP networks. The DHCP Server holds an IP address pool and when a DHCP Client request for an IP address, the DHCP Server picks an IP address from the pool and assigns it to the client. DHCP Server also manages other IP information such as Default Gateway and DNS Server. DHCP is extremely useful to configure the IP information for several devices. Only the administrator can enable the DHCP Client for each device and setup the DHCP Server. The clients will then obtain a unique IP address and other IP settings to connect to the network.

DHCP SERVER BINDING

Apart from dynamically allocating an IP address to a DHCP Client, the DHCP Server also provides a function to manually assign a static IP address to the device with a specific MAC Address. This is called as DHCP Server Binding.

DHCP RELAY/OPTION82

In a large network, there might be several subnets existed and the DHCP Client is not able to serve by DHCP Servers directly. In this case, we need a relay agent to help to transmit the request frames to the DHCP Servers. When a relay agent receives the broadcast request frame from a DHCP Client, the relay agent will transmit the frame to the DHCP Servers, which are in the same subnet by unicast.

Option 82 is an information option to identify the clients by Circuit ID and Remote ID. The Circuit ID is an identity containing the interface name and/or VLAN information, and the Remote ID is to identify the remote host (the relay agent). The DHCP Server can distribute an IP address to the DHCP Client according to Option 82 information and make the IP addresses more controllable.

The frame format for the Circuit ID is as below:

##### VLAN

The VLAN field is for the management VLAN ID, which is natively set to 1.

##### Module

The stack number for the device sending the DHCP request is on. For industrial switches, this byte is always filled as 0.

##### Port

The port number identifies the incoming DHCP request frame/DHCP Client.

The frame format for the Remote ID is as below:

##### MAC Address

By default, the MAC address is set to the MAC address of DHCP relay agent.

CONFIGURE DHCP CLIENT

##### IPv4 Mode

Set the IPv4 Mode to “DHCP Client” to enable the DHCP Client. The system sends a

discovery frame to the network and tires to obtain an IP address from the DHCP Server. After enabling the DHCP Client, users need to connect to the Console Port to get the IP address by using “show ip address” on the CLI.

  - (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE DHCP SERVER INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Server Status

Shows the status of the DHCP server: Down or Up.

##### Server Mode

“Enable” or “Disable” the DHCP Server function.

##### Start IP Address

Set the range of the IP pool. The “Start IP Address” is the starting.

“Start IP Address” must be in the same subnet as that of the switch itself.

##### End IP Address

Set the range of IP pool. The “End IP Address” is the end.

“End IP Address” must be in the same subnet as that of the switch itself.

##### Default Gateway

Set the Default Gateway for the DHCP Clients to make them connect to the WAN.

“Default Gateway” must be in the same subnet as that of the switch itself.

##### DNS Server

Set the DNS Server for the DHCP Clients to make them connect to another device based on the URL instead of IP address.

##### Lease Time

DHCP Server leases an IP address to a device for a period. When the lease time expires, the DHCP server may assign a different IP address in the pool to the device.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

DHCP LEASED TABLE

##### IP Address

This field implies the IP Address that this device acquired from DHCP Server.

##### MAC Address

The MAC Address of the device that acquired mapped IP Address. Administrators can use MAC Address to map to the device’s IP Address.

##### Expired Time

The Expired Time implies the deadline of designated IP Address that leased from DHCP Server. After Expired Time, the DHCP Client must communicate with DHCP Server and ask for the IP Address again.

CONFIGURE DHCP SERVER BINDING INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Binding ID

An ID used to identify the binding.

The range of the Binding ID is from 1 to 32.

##### MAC Address

The device with the specified MAC Address will be assigned to the static Binding IP Address.

##### Binding IP Address

A static IP Address will be assigned to the specified MAC Address.

	: Click the plus icon to add a DHCP Binding row.

	: Click the remove icon to delete the DHCP Binding row.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE DHCP RELAY INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Relay Basic Settings

- Relay Mode

“Enable” or “Disable” the DHCP Relay function.

- Relay Option82

“Enable” or “Disable” the DHCP Relay with Option82 tag.

- Helper Address 1 - 4

The IP Addresses of the DHCP Servers provide IP addresses to the DHCP Clients. A backup of Four Helper Addresses are available during breakdown.

##### Relay Untrust

- Port

Port1 to Port N, where N is based on the total port number.

- Untrust Status

“Enable” or “Disable” to untrust the specific port. If the untrusted status is enabled on a port, the system will drop the DHCP management frames on the port.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

PoE (PoE Model Only)

The PoE, or Power over Ethernet, allows switches to provide electric power along with data on the twisted pair Ethernet cables. The Power over Ethernet defined in IEEE 802.3af provides up to

15.4 W and IEEE 802.3at provides up to 25.5 W. It requires category 5 cables or better to support high power levels. PoE is helpful when the AC power is not available or is available with high cost. It is usually used in surveillance IP cameras, I/O sensors, wireless access points, and IP telephones.

POWER DE-RATING PROTECTION

Due to the power supply is designed inside the devices for some models, so the power budget will decrease by the operating temperature. To ensure the functionality of PoE, we do the protection by software in the background and adjust the budget as temperature rises. Please refer to the Hardware User Manual for the detail of the relationship of power budget and temperature.

POE DEBUG CODE

| Code | Description |
| --- | --- |
| 0x00 | PoE port is on. |
| 0x01 |  |
| 0x02 |  |
| 0x03 |  |
| 0x04 |  |
| 0x06 | PoE port is off. The primary voltage is higher than maximum voltage limitation. |
| 0x07 | PoE port is off. The primary voltage is lower than minimum voltage limitation. |
| 0x11 | PoE port is not defined yet, please check the PoE power input. |
| 0x20 | PoE port is off because of power budget exceeded. |
| 0x1F | PoE port is off because of over-load state according to 802.3AF/AT. |
| 0x43 | PoE port is off because of class error. |
| 0x81 | 802.3BT - compliant PD was detected using BT Port (30w) |
| 0x85 | 802.3BT - SSPD was detected using BT Port (60w/95w) and operates as BT Port (30w) if requested class =< 4. |
| 0x86 | 802.3BT - SSPD was detected using BT Port (60w¦95w) and operates as BT Port (60w/95w) if requested class > 4. |
| 0x90 | BT Port (30w) and delivers power due to force power command. |

We provide PoE Debug Command on the “CLI” for troubleshooting. When users find that the PoE functions work abnormal, users can use the command to acquire the error code. The error codes are mapping to different situations, users can understand the error codes from the following table:

| 0x91 | BT Port (60w/95w) and delivers power due to force power command. |
| --- | --- |
| 0x1B | PoE port is off because detection is in process. |
| 0xA8 | PoE port is not connected. |
| Others | Please contact your system administrator!! |

#### CONFIGURE POWER OVER ETHERNET (POE)

##### Port

Port1 to PortN, where N is based on the total PoE port number.

##### Mode

“Enable”, “Disable”, or “Force” PoE function on the specific port. If the mode is configured to “Force”, the system will provide power forcedly on the specific port even there is no device connected to this port.

##### Status

The field shows the PoE status of the specific port.

On: PoE is enabled or configured to force on the port and power is delivered on the port. Off: PoE is enabled on the port but no Powered Device (PD) is connected.

Disabled: PoE is disabled on the port.

##### Class

The field shows the class followed by the PD. The acceptable power of the class is defined in the IEEE 802.3af/at.

##### Voltage

This field shows the output voltage that PSE provided. The power output of the boost switch will be boosted to 53V.

##### Power

The Consumption field contains provided power in watts. The PSE can provide up to 30Watts and the PDs can receive up to 25.5Watts.

- (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE POE KEEP ALIVE

##### Port

For more information, hover the mouse over the	icon in the system.

Port1 to PortN, where N is based on the total PoE port number.

##### Detect

“Enable” or “Disable” to detect the Powered Device (PD) on the specific port. When the detection is enabled, the system pings the configured IP Address on every Ping Interval.

##### IP Address

The field is the IP Address of the Powered Device (PD).

##### Ping Interval

The Ping Interval is the duration to ping the Powered Device (PD). The range of the Ping Interval is from 1 to 65535 seconds.

The default Ping Interval is 30 seconds.

##### Hold Time

The Hold Time is used when the ping fails. The system will wait for the Hold Time to expire and then try to ping the PD again.

The range of the Hold Time is from 1 to 65535 seconds.

The default Hold Time is 60 seconds.

- (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE POE SCHEDULE

##### Port Selector

Select the port number to configure the PoE Schedule.

Port1 to PortN, where N is based on the total PoE port number.

##### Schedule Mode

“Enable” or “Disable” to provide power by the schedule on the specific port.

- Enable (for each day)

The week is from Sunday to Saturday.

- Week (The x-ray of the table)

The week is from Sunday to Saturday.

- Hour (The y-ray of the table)

The hour is from 00 (00:00) to 23 (23:00).

Users can select the checkbox with the Week and Hour in the table to enable the PoE Schedule on the specific time. For example, if the user wants the PoE to be enabled only on Monday from 6:00 to 7:00 and on Wednesday from 13:00 to 15:00, the following checkboxes must be selected – “Mon-06”, “Mon-07”, “Wed-13”, “Wed-14”, and “Wed-15”.

           (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE POE PRIORITY

From v1.1.48, we remove “Priority Mode” and “Power Limit” for each port configurations in the PoE Priority Page because of the support of the PoE chipset.

From v1.1.77, all PoE Models (including MP/MT/MH/MQ/CP/CT/CH/CQ) support PoE Priority function including 60W/95W 802.3bt switches.

For more information, hover the mouse over the	icon in the system.

##### Basic Setting

  - Power Budget

This field defines the maximum power that can provide to all the connected PDs. The range of Power Budget is from 1 to 240 Watt.

The default Power Budget is 240 Watt.

##### Power Settings

  - Port

Port1 to PortN, where N is based on the total PoE port number.

  - Priority

Assign the PoE priority to high, middle, or low for the specific port.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Industrial Protocols

There are three industrial protocols provided in the switch – EtherNet/IP, PROFINET, and

Modbus/TCP.

EtherNet/IP is an industrial network protocol that linked up the Common Industrial Protocol (CIP) with standard Ethernet. EtherNet/IP takes advantage of both Internet Protocol suite and IEEE 802 standard, which are the most widely deployed collections of Ethernet standards, to define the features and functions for its transportation, networking, data link and physical layers. CIP makes use of object-oriented design to provide EtherNet/IP with the services and device profiles needed for real-time control applications. The object-oriented design of the CIP is also used to promote consistent implementation of automation functions into a diverse ecosystem of products. EtherNet/IP defines how to organize the data in a TCP/UDP packet and transfers the packet in the application layer.

Modbus is a popular communication protocol used for the industrial serial devices. It is usually working as “master-slave” architecture and working with programmable logic controllers which are also called PLCs. The Modbus/TCP implies to provide Modbus Messaging service on the TCP/IP, so that the devices which are running Modbus can communicate with each other with Modbus messages. The Modbus messages are encapsulated with an Ethernet TCP/IP wrapper based on the standard. During the transmission, the switches can only acquire the encapsulated information when the Modbus/TCP is enabled. If users would like to understand the real content of Modbus message, users must install other utilities such as “ModScan”. Our switches implement the Modbus/TCP registers including system information, firmware information, port information, and packet information. The details refer to the “Modbus Data Mapping Information” section.

PROFINET is a technical standard for automation data communication over Industrial Ethernet. It is designed for collecting data and controlling devices in industrial systems. PROFINET is maintained and supported by PROFIBUS & PROFINET International (PI). It defines entire data exchange not only IO-controllers and IO-devices but also parameter setting and diagnosis. PROFINET is useful for production and process automation, safety applications, and all range of drive technology while these applications are implemented.

MODBUS DATA FORMAT AND FUNCTION CODE

The primary four types of Modbus/TCP data format are as following:

| Data Access Type |  | Function Code | Function Name |
| --- | --- | --- | --- |
| Bit Access | Physical Discrete Inputs | 2 | Read Discrete Inputs |
|  | Internal Bits or Physical Coils | 1 | Read Coils |
| Word Access (16-bit Access) | Physical Input Registers | 4 | Read Input Registers |
|  | Physical Output Registers | 3 | Read Holding Registers |

#### MODBUS DATA MAPPING INFORMATION

In the following tables, we assume the total port number is 28.

The following table is for Function Code 3 (Holding Registers) / Function Code 6.

| Address Offset | Data Type | Interpretation | Description |  |
| --- | --- | --- | --- | --- |
| System Information |  |  |  |  |
| 0x0000 to 0x0008 | 1 word | HEX | Port 1 to Port 8 Status Configuration |  |
|  |  |  | 0x0000: | Disable |
|  |  |  | 0x0001: | Enable |

| Address Offset | Data Type | Interpretation | Description |  |  |
| --- | --- | --- | --- | --- | --- |
| System Information |  |  |  |  |  |
| 0x0030 | 20 words | ASCII | Product Name = “MT-0804G” |  |  |
|  |  |  | Word 0 Hi byte = |  | ‘M’ |
|  |  |  | Word 0 Lo byte = |  | ‘T’ |
|  |  |  | Word 1 Hi byte = |  | ‘-‘ |
|  |  |  | Word 1 Lo byte = |  | ‘0’ |
|  |  |  | Word 2 Hi byte = |  | ‘8’ |
|  |  |  | Word 2 Lo byte = |  | ‘0’ |
|  |  |  | Word 3 Hi byte = |  | ‘4’ |
|  |  |  | Word 3 Lo byte = |  | ‘G’ |
| 0x0050 | 1 word |  | Product Serial Number |  |  |
| 0x0051 | 2 words | HEX | Firmware Version For example: |  |  |
|  |  |  | Word 0 = | 0x0103 |  |
|  |  |  | Word 1 = | 0x0200 |  |

The following table is for Function Code 4 (Input Registers). The data map addresses in the following table starts from Modbus address 30001. For example, the address offset 0x0000H equals Modbus address 30001, and the address offset 0x0030H equals Modbus address 30049. All the information read from our switches is in the HEX mode and users can refer to the ASCII table for the translation (e.g., 0x4B=’K’, 0x74=’t’).

|  |  |  | Firmware version is 1.3.2 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 0x0053 | 2 words | HEX | Firmware Release Date For example: |  |  |  |
|  |  |  | Word 0 = |  | 0x1719 |  |
|  |  |  | Word 1 = |  | 0x1506 |  |
|  |  |  | Firmware was released on 2015-06-17 at 19 o’clock |  |  |  |
| 0x0056 | 3 words | HEX | Ethernet MAC Address Ex: MAC = 01:02:03:0A:0B:0C |  |  |  |
|  |  |  | Word 0 Hi byte = |  |  | 0x01 |
|  |  |  | Word 0 Lo byte = |  |  | 0x02 |
|  |  |  | Word 1 Hi byte = |  |  | 0x03 |
|  |  |  | Word 1 Lo byte = |  |  | 0x0A |
|  |  |  | Word 2 Hi byte = |  |  | 0x0B |
|  |  |  | Word 2 Lo byte = |  |  | 0x0C |
| 0x0059 | 1 word | HEX | Power 1 |  |  |  |
|  |  |  | 0x0000: | Off |  |  |
|  |  |  | 0x0001: | On |  |  |
| 0x005A | 1 word | HEX | Power 2 |  |  |  |
|  |  |  | 0x0000: | Off |  |  |
|  |  |  | 0x0001: | On |  |  |
| 0x005B | 1 word | HEX | Fault LED Status |  |  |  |
|  |  |  | 0x0000: | Boot error |  |  |
|  |  |  | 0x0001: | Normal |  |  |
|  |  |  | 0x0002: | Fault |  |  |
| 0x0082 | 1 word | HEX | DO1 |  |  |  |
|  |  |  | 0x0000: | Off |  |  |
|  |  |  | 0x0001: | On |  |  |
| Port Information |  |  |  |  |  |  |
| 0x1000 to 0x1008 | 1 word | HEX | Port 1 to Port 8 Status |  |  |  |
|  |  |  | 0x0000: | Link down |  |  |
|  |  |  | 0x0001: | Link up |  |  |
|  |  |  | 0x0002: | Disable |  |  |
|  |  |  | 0xFFFF: | No port |  |  |
| 0x1100 to 0x1108 | 1 word | HEX | Port 1 to Port 8 Speed |  |  |  |
|  |  |  | 0x0000: | 10M-Half |  |  |
|  |  |  | 0x0001: | 10M-Full |  |  |
|  |  |  | 0x0002: | 100M-Half |  |  |
|  |  |  | 0x0003: | 100M-Full |  |  |

|  |  |  | 0xFFFF: | No port |  |
| --- | --- | --- | --- | --- | --- |
| 0x1200 to 0x1208 | 1 word | HEX | Port 1 to Port 8 Flow Ctrl |  |  |
|  |  |  | 0x0000: | Off |  |
|  |  |  | 0x0001: | On |  |
|  |  |  | 0xFFFF: | No port |  |
| 0x1300 to 0x1313 (Port 1) 0x1314 to 0x1327 (Port 2) … 0x138C to 0x139F (Port 8) | 20 words | ASCII | Port 1 to Port 8 Description Port Description = “100Tx,RJ45.” |  |  |
|  |  |  | Word 0 Hi byte = |  | ‘1’ |
|  |  |  | Word 0 Lo byte = |  | ‘0’ |
|  |  |  | Word 1 Hi byte = |  | ‘0’ |
|  |  |  | Word 1 Lo byte = |  | ‘T’ |
|  |  |  | … |  |  |
|  |  |  | Word 4 Hi byte = |  | ‘4’ |
|  |  |  | Word 4 Lo byte = |  | ‘5’ |
|  |  |  | Word 5 Hi byte = |  | ‘.’ |
|  |  |  | Word 5 Lo byte = |  | ‘\0’ |
| 0x1500 to 0x1508 | 1 Word | HEX | Port 1 to Port 8 PoE Status 0x0000: PoE Off 0x0001: PoE On |  |  |
| 0x1600 to 0x1608 | 1 Word | HEX | Port 1 to Port 8 PoE Power in Watt |  |  |
| Packet Information |  |  |  |  |  |
| 0x2000 to 0x200F | 2 words | HEX | Port 1 to Port 8 Tx Packets Ex: port 1 Tx Packet Amount = 13248635 Received Modbus response: 0x13248635 |  |  |
|  |  |  | Word 0 = | 1324 |  |
|  |  |  | Word 1 = | 8635 |  |
| 0x2080 to 0x208F | 2 words | HEX | Port 1 to Port 8 Tx Bytes Ex: port 1 Tx Bytes Amount = 13248635 Received Modbus response: 0x13248635 |  |  |
|  |  |  | Word 0 = | 1324 |  |
|  |  |  | Word 1 = | 8635 |  |
| 0x2100 to 0x21(YY*2-1) | 2 words | HEX | Port 1 to YY Rx Packets Ex: port 1 Rx Packet Amount = 13248635 Received Modbus response: 0x13248635 |  |  |
|  |  |  | Word 0 = | 1324 |  |
|  |  |  | Word 1 = | 8635 |  |
| 0x2180 to 0x218F | 2 words | HEX | Port 1 to Port 8 Rx Bytes Ex: port 1 Rx Bytes Amount = 13248635 Received Modbus response: 0x13248635 |  |  |

|  |  |  | Word 0 = | 1324 |
| --- | --- | --- | --- | --- |
|  |  |  | Word 1 = | 8635 |

ETHERNET/IP CIP OBJECT MAPPING INFORMATION

The following communication objects that defined in Common Industrial Protocol (CIP) are supported in switches for PLCs and SCADA systems to monitor:

- Identity Object

- TCP/IP Interface Object

- Ethernet Link Object

- Proprietary Object

The following tables introduce the supported attributes, including access rules for each attribute, and services for the above objects. Users can also refer to the official documents of CIP introduction (Vol. 1) and the Ethernet/IP Adaption of CIP (Vol. 2) to understand the details of each attribute of  the standard objects.

Identity Object

The Class code of Identity object is defined in CIP Vol 1, 5-2 and the value is 0x01. Class Attribute List

| Addr ID | Access Rule | Name | Data Type | Description |
| --- | --- | --- | --- | --- |
| 1 | Get | Revision | UINT (16) | Revision of this object |
| 2 | Get | Max Instance | UINT (16) | Maximum instance number of an object currently created in this class level of the device |
| 3 | Get | Number of Instances | UINT (16) | Number of object instances currently created in this class level of the device. |
| 6 | Get | Maximum ID Number Class Attributes | UINT (16) | The attribute ID number of the last class attribute of the class definition implemented in the device |
| 7 | Get | Maximum ID Number Instance Attributes | UINT (16) | The attribute ID number of the last instance attribute of the class definition implemented in the device |

Instance Attribute List

| Addr ID | Access Rule | Name | (Struct.) | Data Type | Description |
| --- | --- | --- | --- | --- | --- |
| 1 | Get | Vendor ID |  | UINT (16) | The vendor ID of company |
| 2 | Get | Device Type |  | UINT (16) | 0x0, “Managed Ethernet Switch” |

| 3 | Get | Product Code |  | UINT (16) | N/A |
| --- | --- | --- | --- | --- | --- |
| 4 | Get | Revision |  | (Struct.) | The version of the Identity object |
|  |  |  | Major | USINT (8) | The structure member, major |
|  |  |  | Minor | USINT (8) | The structure member, minor |
| 5 | Get | Status |  | WORD (16) | Not used |
| 7 | Get | Product Name |  | SHORT_ STRING | The product name in human-readable format |
| 101 | Get | Serial Number |  | UDINT (32) | The serial number of each device |

Common Service List

| Service Code | Implementation |  | Service Name | Description |
| --- | --- | --- | --- | --- |
|  | Class | Instance |  |  |
| 0x01 | ✓ | ✓ | Get_Atributes_All | Return the contents of all attributes of the class |
| 0x0E | ✓ | ✓ | Get_Atributes_Single | Used to read an object instance attribute |
| 0x10 |  | ✓ | Set_Atributes_Single | Used to write an object instance attribute |
| 0x05 |  | ✓ | Reset | Invokes the reset service for the device |

TCP/IP Interface Object

The Class code of TCP/IP Interface object is defined in CIP Vol 2, 5-3 and the value is 0xf5. Class Attribute List

| Addr ID | Access Rule | Name | Data Type | Description |
| --- | --- | --- | --- | --- |
| 1 | Get | Revision | UINT (16) | Revision of this object |
| 2 | Get | Max Instance | UINT (16) | Maximum instance number of an object currently created in this class level of the device |
| 3 | Get | Number of Instances | UINT (16) | Number of object instances currently created in this class level of the device. |
| 6 | Get | Maximum ID Number Class Attributes | UINT (16) | The attribute ID number of the last class attribute of the class definition implemented in the device |
| 7 | Get | Maximum ID Number Instance Attributes | UINT (16) | The attribute ID number of the last instance attribute of the class definition implemented in the device |

Instance Attribute List

| Addr ID | Access Rule | Name | (Struct.) | Data Type | Description |
| --- | --- | --- | --- | --- | --- |
| 1 | Get | Status |  | DWORD | Interface status |

|  |  |  |  | (32) | 0 = The Interface Configuration attribute has not been configured. 1 = The Interface Configuration attribute contains valid configuration obtained from BOOTP, DHCP or non-volatile storage |
| --- | --- | --- | --- | --- | --- |
| 2 | Get | Configuration Capability |  | DWORD (32) | Interface capability flags Bit map of capability flags: Bit 0: BOOTP Client Bit 1: DNS Client Bit 2: DHCP Client Bit 3: DHCP-DNS Update Bit 4: Configuration Settable |
| 3 | Get/Set | Configuration Control |  | DWORD (32) | Interface control flags Bit map of control flags: Bit 0 to 3: Startup Configuration 0 = The device shall use the interface configuration values previously stored (for example, in non-volatile memory or via hardware witches). 1 = The device shall obtain its interface configuration values via BOOTP. 2 = The device shall obtain its interface configuration values via DHCP upon start-up. 3 to15 = Reserved. |
| 4 | Get | Physical Link Object |  | (Struct.) | Path to physical link object |
|  |  |  | Path Size | UINT (16) | Size of Path |
|  |  |  | Path | Padded EPATH | Logical segments identifying the physical link object |
| 5 | Get/Set | Interface Configuration |  | (Struct.) | TCP/IP network interface configuration |
|  |  |  | IP Address | UDINT (32) | The device’s IP address |

|  |  |  | Network Mask | UDINT (32) | The device’s network mask |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Gateway Address | UDINT (32) | Default gateway address |
|  |  |  | Name Server | UDINT (32) | Primary name server |
|  |  |  | Name Server 2 | UDINT (32) | Secondary name server |
|  |  |  | Domain Name | STRING | Default domain name |
| 6 | Get/Set | Host Name |  | UDINT (32) | Host name |

Common Service List

| Service Code | Implementation |  | Service Name | Description |
| --- | --- | --- | --- | --- |
|  | Class | Instance |  |  |
| 0x01 | ✓ | ✓ | Get_Atributes_All | Return the contents of all attributes of the class |
| 0x0E | ✓ | ✓ | Get_Atributes_Single | Used to read an object instance attribute |
| 0x10 |  | ✓ | Set_Atributes_Single | Used to write an object instance attribute |

Ethernet Link Object

The Class code of TCP/IP Interface object is defined in CIP Vol 2, 5-4 and the value is 0xf6. There is an instance for each switch port, and mapping as the following table:

| Instance Number | Mapping to |
| --- | --- |
| 0 | Ethernet Link class |
| 1 | 1st switch port |
| 2 | 2nd switch port |
| 3 | 3rd switch port |
| … | Nth switch port |

Class Attribute List

| Addr ID | Access Rule | Name | Data Type | Description |
| --- | --- | --- | --- | --- |
| 1 | Get | Revision | UINT (16) | Revision of this object |
| 2 | Get | Max Instance | UINT (16) | Maximum instance number of an object currently created in this class level of the device |
| 3 | Get | Number of Instances | UINT (16) | Number of object instances currently created in this class level of the device. |
| 6 | Get | Maximum ID Number | UINT (16) | The attribute ID number of the last |

|  |  | Class Attributes |  | class attribute of the class definition implemented in the device |
| --- | --- | --- | --- | --- |
| 7 | Get | Maximum ID Number Instance Attributes | UINT (16) | The attribute ID number of the last instance attribute of the class definition implemented in the device |

Instance Attribute List

| Addr ID | Access Rule | Name | (Struct.) | Data Type | Description |
| --- | --- | --- | --- | --- | --- |
| 1 | Get | Interface Speed |  | UDINT (32) | Interface speed currently in use (Speed in Mbps, e.g., 0, 10, 100, 1000, 10000, etc.) |
| 2 | Get | Interface Flags |  | DWORD (32) | Refer to the Interface Flags table |
| 3 | Get | Physical Address |  | ARRAY of 6 USINT (8) | MAC layer address (The System MAC address) |
| 4 | Get | Interface Counters |  | (Struct.) | Counters relevant to the receipt of packets |
|  |  |  | In Octets | UDINT (32) | Octets received on the interface. |
|  |  |  | In Ucast Packets | UDINT (32) | Unicast packets received on the interface |
|  |  |  | In NUcast Packets | UDINT (32) | Non-unicast packets received on the interface |
|  |  |  | In Discards | UDINT (32) | Inbound packets received on the interface but are discarded |
|  |  |  | In Errors | UDINT (32) | Inbound packets that contain Errors (does not include In Discards) |
|  |  |  | In Unknown Protos | UDINT (32) | Inbound packets with unknown protocol |
|  |  |  | Out Octets | UDINT (32) | Octets sent on the interface |
|  |  |  | Out Ucast Packets | UDINT (32) | Unicast packets sent on the interface |
|  |  |  | Out NUcast Packets | UDINT (32) | Non-unicast packets sent on the interface |
|  |  |  | Out Discards | UDINT (32) | Discarded outbound packets |
|  |  |  | Out Errors | UDINT (32) | Outbound packets that contain errors |
| 6 | Get/Set | Interface |  | (Struct.) | Configuration for physical interface |

|  |  | Control | Control Bits | WORD (16) | Bit 0: Auto-Negotiate Value 0: Force Value 1: Auto-Nego Bit 1: Half/Full Duplex Value 0: half duplex Value 1: full duplex Bit 2 to 15: Reserved, all zero |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Forced Interface Speed | UINT (16) | Speed at which the interface shall be forced to operate |
| 7 | Get | Interface Type |  | USINT | Value 0: Unknown interface type. Value 1: The interface is internal to the device, for example, in the case of an embedded switch. Value 2: Twisted-pair (e.g., 10Base-T, 100Base-TX, 1000Base-T, etc.) Value 3: Optical fiber (e.g., 100Base-FX) Value 4 to 256: Reserved |
| 8 | Get | Interface State |  | USINT | Value 0: Unknown interface state Value 1: The interface is enabled and is ready to send and receive data Value 2: The interface is disabled Value 3: The interface is testing Value 4 to 256: Reserved |
| 9 | Get | Admin State |  | USINT | Value 0: Reserved Value 1: Enable the interface Value 2: Disable the interface. If this is the only CIP communications interface, a request to disable the interface shall result in an error (status code 0x09). Value 3 to 256: Reserved |
| 10 | Get | Interface Label |  | SHORT_ STRING | Human readable identification |
| 101 | Get | PoE Status |  | USINT (8) | Value 1: PoE On Value 2: PoE Off |

| 102 | Get | PoE Power |  | UDINT (32) | PoE Power in Watt |
| --- | --- | --- | --- | --- | --- |
| 103 | Get/Set | PoE Mode |  | UDINT (32) | Value 0: Unknown Value 1: Enable Value 2: Disable Value 3: Force |

Interface Flags

| Bit(s) | Called | Definition |
| --- | --- | --- |
| 0 | Link Status | - indicates an inactive link. - indicates an active link. |
| 1 | Half/Full Duplex | - indicates half duplex. - indicates full duplex. |
| 2-4 | Negotiation Status | Indicates the status of link auto-negotiation 0 = Auto-negotiation in progress. 1 = Auto-negotiation and speed detection failed. Using default values for speed and duplex. Default values are product-dependent; recommended defaults are 10Mbps and half duplex. 2 = Auto negotiation failed but detected speed. Duplex was defaulted. Default value is product-dependent; recommended default is half duplex. 3 = Successfully negotiated speed and duplex. 4 = Auto-negotiation not attempted. Forced speed and duplex. |
| 5 | Manual Setting Requires Reset | 0 indicates the interface can activate changes to link parameters (auto-negotiate, duplex mode, interface speed) automatically. 1 indicates the device requires a Reset service be issued to its Identity Object for the changes to take effect. |
| 6 | Local Hardware Fault | 0 indicates the interface detects no local hardware fault; 1 indicates a local hardware fault is detected. The meaning of this is product-specific. For example, an AUI/MII interface might detect no transceiver attached, or a radio modem might detect no antenna attached. In contrast to the soft, possibly self-correcting nature of the Link Status being inactive, this is assumed a hard-fault requiring user intervention. |
| 7-31 | Reserved | Shall be set to zero |

Common Service List

| Service Code | Implementation |  | Service Name | Description |
| --- | --- | --- | --- | --- |
|  | Class | Instance |  |  |
| 0x0E | ✓ | ✓ | Get_Atributes_Single | Used to read an object instance attribute |
| 0x10 |  | ✓ | Set_Atributes_Single | Used to write an object instance attribute |

Proprietary Object

The Class code of Proprietary object is defined by vendor, and the value is 0x1C1. Class Attribute List

| Addr ID | Access Rule | Name | Data Type | Description |
| --- | --- | --- | --- | --- |
| 1 | Get | Power 1 | USINT (8) | Power 1 status. Value 1: On Value 0: Off |
| 2 | Get | Power 2 | USINT (8) | Power 2 status. Value 1: On Value 0: Off |
| 3 | Get | Alarm Relay | USINT (8) | Alarm Relay status. Value 1: On Value 0: Off |
| 4 | Get | Digital Input | USINT (8) | Digital Input status. Value 1: High Value 0: Low |
| 5 | Get | System Time | UDINT (32) | System Time encodes as UNIX time. |
| 6 | Get | All Interface Speed | ARRAY of 28 UDINT(32) | Array list of all interface speed currently in use |
| 7 | Get | All Interface Flags | ARRAY of 28 DWORD(32) | Array list of all interface flags. Refer to the Interface Flags table |
| 8 | Get | All Interface States | UDINT (32) | Bitwise of all current interface states. Bit 0: Port 1 Value 0: Link down Value 1: Link up Bit 1: Port 2, and so on |

ETHERNET/IP ELECTRONIC DATA SHEET (EDS) FILE

The EDS (Electronic Data Sheet) file includes electronic descriptions of all relevant communication parameters and objects of an EtherNet/IP device. It is required for I/O controllers to recognize switch and its CIP capability.

The list includes the sections which are described in our EDS file.

- [File]

- [Device]

- [Device Classification]

- [Port]

- Icon should be 32 * 32 in pixel.

PROFINET PARAMETERS MAPPING INFORMATION

There are three categories of parameters – Device Parameters, Device Status, and Port Parameters.

- r/w: Read and Write

- ro:	Read Only

### Device Parameters

| Byte | Name | Access | Value | Description | Default Value |
| --- | --- | --- | --- | --- | --- |
| 0 | Status Alarm | rw | 0 | Do not send any alarms | 0: No Alarms |
|  |  |  | 1 | Send alarm if any status change |  |
| 1 | Power Alarm 1 | rw | 0 | Do not send power failed alarms | 0: No Alarms |
|  |  |  | 1 | Send alarm if power supply 1 fails |  |
| 2 | Power Alarm 2 | rw | 0 | Do not send power failed alarms | 0: No Alarms |
|  |  |  | 1 | Send alarm if power supply 2 fails |  |

Device Status

| Byte | Name | Access | Value | Description |
| --- | --- | --- | --- | --- |
| 0 | Overall Device Status | ro | 0 | Unavailable |
|  |  |  | 1 | OK |
|  |  |  | 2 | Device Error |
| 1 | Fault Status | ro | 0 | Unavailable |
|  |  |  | 1 | OK |
|  |  |  | 2 | Device Detect Fault |
| 2 | Power 1 Status | ro | 0 | Unavailable |
|  |  |  | 1 | OK |
|  |  |  | 2 | Power 1 Fails |
| 3 | Power 2 Status | ro | 0 | Unavailable |
|  |  |  | 1 | OK |
|  |  |  | 2 | Power 2 Fails |
| 4 | Relay 1 | ro | 0 | Unavailable |
|  |  |  | 1 | Closed |

|  |  |  | 2 | Open |
| --- | --- | --- | --- | --- |
| 5 | Relay 2 | ro | 0 | Unavailable |
|  |  |  | 1 | Closed |
|  |  |  | 2 | Open |
| 6 | Redundant Mode | ro | 0 | Unavailable |
|  |  |  | 1 | RSTP |
|  |  |  | 2 | ERPS |
|  |  |  | 3 | ERPS Sub-ring 1 |
|  |  |  | 4 | ERPS Sub-ring 2 |
| 7 | Ring Status | ro | 0 | Unavailable |
|  |  |  | 1 | Healthy |
|  |  |  | 2 | Break |
| 8 | Redundant Port 1 Status | ro | 0 | Unavailable |
|  |  |  | 1 | Forwarding |
|  |  |  | 2 | Blocking |
|  |  |  | 3 | Link Down |
| 9 | Redundant Port 2 Status | ro | 0 | Unavailable |
|  |  |  | 1 | Forwarding |
|  |  |  | 2 | Blocking |
|  |  |  | 3 | Link Down |
| 10 | Sub-ring Mode | ro | 0 | Unavailable |
|  |  |  | 1 | Healthy |
|  |  |  | 2 | Break |
| 11 | Sub-ring Port 1 Status | ro | 0 | Unavailable |
|  |  |  | 1 | Forwarding |
|  |  |  | 2 | Blocking |
|  |  |  | 3 | Link Down |
| 12 | Sub-ring Port 2 Status | ro | 0 | Unavailable |
|  |  |  | 1 | Forwarding |
|  |  |  | 2 | Blocking |
|  |  |  | 3 | Link Down |
| 13 | Connection | ro | 0 | Unavailable |
|  |  |  | 1 | OK |
|  |  |  | 2 | Connection Failure |

Port Parameters

| Byte | Name | Access | Value | Description |
| --- | --- | --- | --- | --- |
| 0 | Port Alarm | rw | 0 | Off, do net send alarm |

|  |  |  | 1 | On, send alarm when port link down |
| --- | --- | --- | --- | --- |
| 1 | Port Admin State | rw | 0 | Unavailable |
|  |  |  | 1 | Off, inactive |
|  |  |  | 2 | On, active |
| 2 | Port Link State | ro | 0 | Unavailable |
|  |  |  | 1 | Link is down |
|  |  |  | 2 | Link is up |
| 3 | Port Speed | ro | 0 | Unavailable |
|  |  |  | 1 | Unknown |
|  |  |  | 2 | 10M |
|  |  |  | 3 | 100M |
|  |  |  | 4 | 1G |
|  |  |  | 5 | 10G |
| 4 | Port Duplex | ro | 0 | Unavailable |
|  |  |  | 1 | Half |
|  |  |  | 2 | Full |
| 5 | Port Auto-negotiation | ro | 0 | Unavailable |
|  |  |  | 1 | Off |
|  |  |  | 2 | On |
| 6 | Port Flow Control | ro | 0 | Unavailable |
|  |  |  | 1 | Off |
|  |  |  | 2 | On |
| 7 | Port MDI/MDIX | ro | 0 | Unavailable |
|  |  |  | 1 | MDI |
|  |  |  | 2 | MDIX |

#### CONFIGURE INDUSTRIAL PROTOCOLS INFORMATION

Note: For PoE models, the system will take around 10 seconds to read PoE status.

##### Modbus Mode

“Enable” or “Disable” the Modbus/TCP function.

##### Ethernet/IP Mode

“Enable” or “Disable” the Ethernet/IP function.

##### PROFINET Mode

“Enable” or “Disable” the PROFINET function.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# UPnP

UPnP is Universal Plug and Play, a set of networking protocols that permit the network devices to seamlessly discover each other in the networks. It is promoted by the UPnP Forum, but since 2016, all UPnP efforts are managed by the Open Connectivity Foundation.

UPnP extends “plug and play” to connect to a network device without configuration. When an UPnP device such as printer, Wi-Fi AP, or mobile device connects to a network, it will automatically establish the working configurations with another devices.

CONFIGURE UPNP INFORMATION

For more information, hover the mouse over the	icon in the system.

##### UPnP Mode

“Enable” or “Disable” the UPnP function.

##### Advertisement Interval

A period used to send the UPnP advertisement frame.

The range of the Advertisement Interval is from 300 to 86400 seconds.

The default Advertisement Interval is 1800 seconds.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Port Management

Port Management contains a “Description” field that is used to describe the port, “Enable” or “Disable” option to turn on or turn off a specific port, configure the speed-duplex for the port, and Flow Control on the port. In the Port Status page, the users can obtain information such as Link Status, Speed, Duplex, Flow Control, Tx and Rx in Bytes, and PoE status. These are helpful for the administrator to manage the interfaces on the switch.

#### CONFIGURE PORT INFORMATION

##### Port

For more information, hover the mouse over the	icon in the system.

Port1 to PortN, where N is based on the total port number.

##### Description

The description for the port is helpful for the administrator to identify the difference between the ports.

The max. length for the Description is 32 characters.

Note: #, \, ', ", ? are invalid characters.

##### Link Status

Link Status shows “Up”, “Down”, or “Disable” to reflect the link status of the port.

##### Admin Status

“Enable” or “Disable” the Admin Status of the port to restrict the transmission on the port. Note: Administrator can turn off the un-used port to secure the network with unexpected device.

##### Speed

The users can manually fix the speed and duplex or automatically run auto-negotiation to determine the speed and duplex for copper ports.

  - Auto: The port follows IEEE 802.3 protocol to auto-negotiate with connected device.

  - 100M-Full: The port transmits frames with 100Mbits per second speed and full duplex.

  - 100M-Half: The port transmits frames with 100Mbits per second speed and half duplex.

  - 10M-Full: The port transmits frames with 10Mbits per second speed and full duplex.

  - 10M-Half: The port transmits frames with 10Mbits per second speed and half duplex.

The users must manually configure SFP ports to fix the speed and duplex. The default setting is the highest speed for the SFP slot.

  - Auto: The port follows IEEE 802.3 protocol to auto-negotiate with connected device.

  - 10G-Full (Only supported on 10G models)

The port transmits frames with 10Gbits per second speed and full duplex.

  - 1G-Full: The port transmits frames with 1Gbits per second speed and full duplex.

  - 100M-Full (Only supported on dual speed SFP ports)

The port transmits frames with 100Mbits per second speed and full duplex.

  - Copper-Full: Select Copper-Full when using copper SFP module.

Note: Configure the port speed to "1G-Full" if users need the VDSL2 SFP supported.

Configure the port speed to “Auto” if the connected device is unmanaged.

For Copper SFP Module, please refer to the following instructions to configure the correct speed:

| Copper SFP Module Type | Speed Config | Note |
| --- | --- | --- |
| SGMII (10/100/1000M) | Copper-Full | Only support transmitting on 1000M |
| Multi-Speed (1G/10G) | 10G-Full | Depends on the connected speed |
| 10G | 10G-Full |  |
| 1G / VDSL2 | 1G-Full |  |

##### Flow Control

“Enable” or “Disable” the Flow Control when the speed is set to “Auto”. Enabling the Flow Control helps to prevent the traffic from losing when the network is in congestion.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

SFP DDM STATUS

##### SFP Port Selector

Select the SFP port number to display SFP DDM information.

##### Transceiver Info

If there is no SFP module inserted or the information cannot be read, the field will show “-“.

  - Vendor Name

This field shows the brand or vendor name of the SFP module.

  - Part Number

This field shows the model’s name (part number) of the SFP module.

  - Transceiver Type

This field shows the transceiver type of the SFP module including transmitting speed and the type of fiber. If there is no SFP module inserted or the transceiver type cannot be read, the field will show “Unknown“.

  - Laser Wavelength

This field shows the laser operating wavelength of the SFP module.

  - Link Length

This field shows the maximum link length of the SFP module.

##### DDM Module

This section only shows when the SFP DDM is supported on the inserted SFP module.

  - Real Time Value

The current operating information including temperature, voltage, current, Tx power, and Rx power.

  - Alarm Warning

The default configured threshold for triggering the alarm and system warning. There are 5 types of information (temperature, voltage, current, Tx power, and Rx power) and 4 levels of alarm and warning (high alarm/warning, low alarm/warning).

#### DETAILED PORT STATUS

There are two methods to link to detailed port status (RMON). One is from menu and the other is from the front panel picture. Uses can directly click the port on the front panel and then the page will redirect to the detailed port status page of the specific port. The RMON is a set of standard Simple Network Management Protocol (SNMP) and it is useful to monitor and manage the incoming and outgoing traffic.

##### Port Selector

Select the port number to monitor the RMON information. Port 1 to N, where N is based on the total port number.

##### Received Packets

  - Rx Octets: the total received traffic in bytes

  - Rx Unicast: the number of received unicast packets

  - Rx Multicast: the number of received multicast packets

  - Rx Broadcast: the number of received broadcast packets

  - Rx Pause: the number of MAC Control packets received on the specific interface with an opcode indicating the PAUSE operation.

##### Received Size Counter

  - Rx 64 Bytes: the number of received packets that were 64 octets

  - Rx 65-127 Bytes: the number of received packets that were from 65 to 127 octets

  - Rx 128-255 Bytes: the number of received packets that were from 128 to 255 octets

  - Rx 256-511 Bytes: the number of received packets that were from 256 to 511 octets

  - Rx 512-1023 Bytes: the number of received packets that  were from 512 to 1023  octets

  - Rx 1024-1518 Bytes: the number of received packets that were from 1024 to 1518 octets

##### Received Error Counter

  - Rx Collision: the total number of collisions on the Ethernet segment.

  - Rx CRC/Alignment: the total number of received packets that have  either  a  bad Frame Check Sequence (FCS) with an integral number of octets (FCS Error) or a bad FCS with a non-integral number of octets (Alignment Error).

  - Rx Drop: the total number of dropped packets due to lack of resources.

  - Rx Fragment: the total number of received packets that are less than 64 octets and    had either a bad Frame Check Sequence (FCS) with an integral number of octets (FCS Error) or a bad FCS with a non-integral number of octets (Alignment Error).

  - Rx Jabber: the total number of received packets that are longer than 1518 octets and had either a bad Frame Check Sequence (FCS) with an integral number of octets (FCS Error) or a bad FCS with a non-integral number of octets (Alignment Error).

  - Rx Oversize: the total number of received packets that are longer than 1518 octets.

  - Rx Undersize: the total number of received packets that are less than 64 octets.

##### Transmitted Packets

  - Tx Octets: the total transmitted traffic in bytes.

  - Tx Unicast: the number of transmitted unicast packets

  - Tx Multicast: the number of transmitted multicast packets

  - Tx Broadcast: the number of transmitted broadcast packets

  - Tx Pause: the number of MAC Control packets transmitted on the specific interface with an opcode indicating the PAUSE operation.

##### Transmitted Error Counter

  - Tx Discard: the number of outbound packets which are chosen to be discarded even though no errors had been detected. One possible reason for discarding such a packet could be to free up buffer space.

  - Tx Error: the number of outbound packets that could not be transmitted because of errors.

EEE STATUS

Energy-Efficient Ethernet (EEE) is a feature to save power when the link is idle, which means the port is linked up but there is no traffic on the link. The EEE function can be enabled or disabled by port.

##### Port

Port 1 to N, where N is based on the total port number.

##### State

Display the state, Enable or Disable, of EEE function.

##### TxIdleTime

The TxIdleTime is the required time to enter the EEE low-power mode.

##### TxWakeupTime

The TxWakeupTime is the required time to exit the EEE low-power mode.

##### TxEventCount

The TxEventCount is the EEE Low Power Idle (LPI) event counter of Tx. This counter implies the number of times that the LPI mode has been enforced by EEE function on the transmitting side.

##### TxDuration

The TxDuration is an LPI event duration on the transmitting path which is updated if the port is in the EEE LPI mode.

##### RxEventCount

The RxEventCount is the EEE LPI event counter of Rx. This counter implies the number of times that the LPI mode has been enforced by EEE function on the receiving side.

##### RxDuration

The RxDuration is an LPI event duration on the receiving path which is updated if the port is in the EEE LPI mode.

##### Enable

Select the specific ports or deselect the selected ports and then click the “Apply Selected” button to enable or disable the EEE function. Directly click “Enable All” to enable EEE function on all ports or “Disable All” to disable EEE function on all ports.

#### PORT STATUS

##### Port

Port 1 to N, where N is based on the total port number.

##### Link Status

Link Status displays the link state (“Up” or “Down”) of the port. If the port is disabled, it displays “Disabled”.

##### Speed

Speed displays the access speed in bit per second of the port. If the port is linked down, it displays “-“.

##### Duplex

Duplex displays the link-type (Full or Half) of the port. If the port is linked down, it displays “-“.

##### Flow Control

It is the state (On or Off) of the Flow Control.

##### Rx Byte

This is the total received frames formatted in byte.

##### Tx Byte

This is the total transmitted frames formatted in byte.

- PoE (PoE Model Only)

PoE displays the PoE state (Delivery, No PD, Disabled, None) of the port. If the port does not support PoE function, it displays “None”.

Note: This information is displayed on the system that supports the PoE function.

##### Clear Rx/Tx

Select the specific ports and click the “Click Selected” button to clear the Tx/Rx Byte information or click “Click All” button to clear all ports’ Tx/Rx Byte information.

# IGMP Snooping

Internet Group Management Protocol (IGMP) is used in communicating among hosts and establishing a multicast group membership on the IPv4 networks (Layer 3). IGMP provides the ability to prune multicast traffic to those who need this kind of traffic and reduce the amount of traffic on the network. However, switches work on the MAC Layer (Layer 2) and are unable to obtain IGMP information. IGMP Snooping allows the switch to listen to the IGMP communication between hosts and routers and maintains a table of multicast IPs and group members. IGMP Snooping can prevent the hosts on the LAN from receiving traffic from a non-joined multicast group and save bandwidth of the network.

CONFIGURE IGMP SNOOPING INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Basic Setting

  - Mode

“Enable” or “Disable” the IGMP Snooping function.

  - Last-Member Count

The count is the number of times that the router sends IGMP query messages to receive the leave message.

The range of the Last-Member Count is from 2 to 10.

The default Last-Member Count Interval is 2.

。 Last-Member Interval

The interval is the period to send IGMP query messages.

The range of the Last-Member Interval is from 1 to 25 seconds.

The default Last-Member Interval is 1 second.

##### Fast-Leave Setting

  - Port

Port 1 to N, where N is based on the total port number.

  - Fast-Leave Mode

“Enable” or “Disable” the fast-leave function on the specific port. If the fast-leave mode is enabled on the port, the switch will close the multicast stream when receiving a leave message on this port without further action.

           (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE IGMP SNOOPING QUERIER INFORMATION

For more information, hover the mouse over the icon in the system.

##### Basic Settings

  - Mode

“Enable” or “Disable” the IGMP Snooping Querier function. If it is enabled, the system sends IGMP snooping version 1 and 2 queries.

  - Querier Interval

This period is the interval to send the IGMP snooping queries. The range of the Querier Interval is from 1 to 3600 seconds. The default Querier Interval is 125 seconds.

  - Query Max Response Time

This is a timer to wait for the member response of the IGMP groups. It is used in

removing the information of the IGMP groups if no member responds to the query.

##### Query Version Settings

The Query Version Settings is configured for per-VLAN query.

  - VLAN ID

The field is to fill in the VLAN ID to configure the IGMP Snooping query version.

  - State

“Enable” or “Disable” the IGMP Snooping query on the configured VLAN ID.

  - Version

Set the IGMP Snooping version (v1, v2c, v3) on the specific VLAN.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE UNKNOWN MULTICAST INFORMATION

##### Action Settings

  - Unknown-Multicast

Configure the action when the system receives an unknown-multicast packet.

Flooding: flood the unknown-multicast packet to all other ports.

Discarding: discard the unknown-multicast packet.

Router: forward the unknown-multicast packet to the router port.

##### Router Port Settings

  - No.

Port 1 to N, where N is based on the total port number.

  - Router Port

Set the specific port to router port or not.

  - Status

The status field shows the port’s status which “-“ implies not a router port and “static” implies set to router port.

IGMP SNOOPING TABLE

##### Multicast IP

The Multicast IP is the IP address of the multicast group.

##### Group

The group shows the port number, which joined the group.

# 802.1Q VLAN

## Q VLAN

Virtual Local Area Network (VLAN) is a structure that can ease Network planning. The devices in a VLAN can be located anywhere without the restriction of physical connections but work like they are on the same physical segment.

IEEE 802.1Q defines VLAN tagging conception for the Ethernet frames. VLAN tagging supports frames in the different VLAN groups transmitting on a link (called VLAN trunk). The maximum number of VLANs on the Ethernet network is 4096. The VLAN 0 and VLAN 4095 are for specific use and hence the usable VLAN number is 4094.

## VLAN Q-IN-Q

VLAN Q-in-Q, also called Stacked VLAN, is an extension for 802.1Q VLAN. It supports a maximum of 4096*4096 VLAN groups. VLAN Q-in-Q can apply a port to a provider, customer, or tunnel for different applications. The header of the stacked VLAN frame contains two 802.1Q Headers with different Ethertype (TPID). The TPID “0x88A8” is the outer tag by default and the TPID “0x8100” is the inner tag for 802.1Q VLAN. Customized ethertype called Specific Provider Ethertype are supported if one or more ports are set to “Specific Provider”.

CONFIGURE 802.1Q VLAN INFORMATION

For more information, hover the mouse over the	icon in the system.

##### VLAN Member Settings

      - VLAN ID

Assigns a unique VLAN ID to this VLAN group. The range of the VLAN ID is from 1 to 4094.

      - Name

Assigns a name to this VLAN group to identify the different VLANs.

The max. length for the Name is 32 characters. Note: #, \, ', ", ? are invalid characters.

      - Untagged Ports

Sets the untagged ports for this VLAN group. The system removes the VLAN tag before transmitting from the port that is set to “untagged”. Usually, this port is connected to the end device that belongs to this VLAN.

      - Tagged Ports

Sets the tagged ports for this VLAN group. The system keeps the VLAN tag when transmitting from the port that is set to “tagged”. Usually, this port is connected to another switch and uses the VLAN tag to transfer the VLAN information.

。   : Click the plus icon to add a VLAN Member row.

。   : Click the remove icon to delete the VLAN Member row.

  - Q VLAN TABLE

##### VLAN ID

This is the assigned unique VLAN ID for this VLAN group.

##### VLAN Name

This is the assigned VLAN Name for this VLAN group.

##### Untag Member

These ports are assigned as VLAN untagged ports.

##### Tag Member

These ports are assigned as VLAN tagged ports.

CONFIGURE 802.1Q VLAN PVID & ACCEPT TYPE

For more information, hover the mouse over the	icon in the system.

##### VLAN PVID

      - Port

Port1 to PortN, where N is based on the total port number.

      - PVID

Assign a VLAN ID to the frames without a VLAN tag that come into the specific port.

##### Accept Type

      - No.

Port1 to PortN, where N is based on the total port number.

      - Filter

Three types of filters are provided: All, Tagged Only, Untagged Only.

All: Accept both tagged and untagged frames that come into the port.

Tagged Only: Accept only tagged frames that come into the port.

Untagged Only: Accept only untagged frames that come into the port.

	   (Apply Button)

After configuring the above fields, click "Apply" button to make it effective.

CONFIGURE VLAN Q-IN-Q

For more information, hover the mouse over the	icon in the system.

##### Specific Provider Ethertype

This is a global configuration and an Ethertype is assigned for all ports, which are configured as “Specific Provider”. This field is locked (disabled) until at least one port is configured to the “Specific Provider” in the “Q-in-Q Port Settings” section.

The range of the Provider Ethertype is from 0x0000 to 0xFFFF, but 0x8100 is invalid.

The default Provider Ethertype is 0x88A8.

##### Q-in-Q Port Settings

      - Port

Port1 to PortN, where N is based on the total port number.

      - Mode

Set the port to one of the Q-in-Q modes.

The Egress is dependent on the connected device and hence the egress action is skipped.

| Mode | Ingress |
| --- | --- |
| Q-in-Q Tunnel | Untagged Frames: Add TPID:0x88A8 tag and forward. Tagged Frames: - TPID:0x8100: Add TPID:0x88A8 tag and forward. - TPID:0x88A8: Forward the frames. |
| Mode | Ingress |
| Customer | A port set to “Customer” runs typically 802.1Q VLAN. Untagged Frames: Add TPID:0x8100 tag and forward. Tagged Frames: 1. TPID:0x8100: - Same VLAN ID: Forward the frames. - Different VLAN ID: Discard the frames. 2. TPID:0x88A8: Discard the frames. |
| Provider | Untagged Frames: Add TPID:0x88A8 tag and forward. Tagged Frames: - TPID:0x8100: Discard the frames. - TPID:0x88A8: - Same VLAN ID: Forward the frames. - Different VLAN ID: Discard the frames. |
| Specific Provider | Users define the Ethertype for the Provider service. Untagged Frames: Add the user-defined TPID tag and forward. Tagged Frames: - TPID:0x8100: Discard the frames. - TPID:0x88A8: Discard the frames. - TPID: [user-defined]: - Same VLAN ID: Forward the frames. - Different VLAN ID: Discard the frames. |

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Quality of Service

Quality of Service which known as QoS provides a stable and predictable transmitting service. It is useful to manage the bandwidth more efficiently based on the requirement of applications. Users can set different priorities for different traffics to satisfy the services which need a fixed bandwidth and have more sensitive of delay. Quality of Service can also optimize the restrict bandwidth resource and control the network traffic of the switches.

#### CONFIGURE QOS INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Queue Scheduling

      - Scheduling Mode

Select the scheduling mode for the Quality of Service.

WRR: Weighted Round Robin. WRR ensures that every queue takes turns to transmit the traffic by its weight.

Strict: Strict Priority Queue. The traffic is transmitted based on the priority, which is from highest to lowest.

##### Queue Weight

      - Queue

Eight queues from queue 0 to queue 7 are supported.

      - Weight

Enables you to configure a specific weight for the port.

The range of the Weight is from 1 to 100. There is no need to sum all queues to 100. The default Weight for each queue is displayed in the table:

| Queue | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Weight | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

CONFIGURE QOS TRUST MODE AND DEFAULT COS

##### Trust Mode

      - Port

Port1 to PortN, where N is based on the total port number.

      - Mode

CoS: Class of Service. Use the 3-bit “PRI” field in the VLAN tag. It enables you to assign traffic to 8 different classes from 0 to 7.

DSCP: Use 6-bit field “DSCP” in the Type of Service (ToS) tag. It enables you to assign traffic to 64 different types from 0 to 63.

##### Default CoS

      - Port

Port1 to PortN, where N is based on the total port number.

      - Class

You can assign a default class to the port. The system follows the assigned CoS classes to transmit frames if there is no VLAN tag in the frame header.

The default Class for each port is 0.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE COS MAPPING

##### Class / Priority

There are 3 bits for the “Class of Service” field called “PRI” in the VLAN tag and there are 8 classes from 0 to 7.

##### Queue

The chipset supports 8 queues from queue 0 to queue 7. The queue 0 is the lowest priority queue and the queue 7 is the highest priority queue.

The default Queue for each class is displayed in the table:

| Class | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Queue | 1 | 0 | 2 | 3 | 4 | 5 | 6 | 7 |

CONFIGURE TOS MAPPING

##### DSCP

There are 6 bits for the “DSCP” in ToS tag and hence there are 64 classes from 0 to 63.

##### Queue

The chipset supports 8 queues from queue 0 to queue 7. The queue 0 is the least priority queue and the queue 7 is the highest priority queue.

The default Queue for each type is displayed in the table:

| Type | 0-7 | 8-15 | 16-23 | 24-31 | 32-39 | 40-47 | 48-55 | 56-63 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Queue | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 |

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Port Trunk

Port Trunk is also known as Link Aggregation, and it is a protocol to group links to a trunk. A total of 8 trunk groups are provided. It is a good method to reach load balance and link backup. For example, when port 1 to port 4 are combined to trunk 1 and all ports support 100Tx and set to full-duplex, the bandwidth of the trunk will be 800Mbps. The traffic transmitting on the trunk is distributed to one of the links by the source MAC address to reach the load balance. When the trunk mode is set to LACP and when one of the links is broken, the traffic will transmit on another link on the group.

#### CONFIGURE PORT TRUNK INFORMATION

##### Group

Eight trunk groups from Trunk 1 to Trunk 8 are supported.

##### Trunking Mode

Two trunking modes are available: “LACP” and “Static”.

Static: The traffic is transmitted on one of the links in the group. The link is determined by the MAC Address in the frame header. If the link is broken, the traffic cannot transmit on the other links in the group.

LACP: It is also known as “Dynamic” trunking. If the current transmitting link is broken, the traffic can be transmitted on another link in the group.

##### Member Ports

Select member ports to be joined in the specified Trunk group. A port can only be in one of the Trunk group. Each Trunk group supports maximum 8 member per ports.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

#### PORT TRUNK STATUS

##### Group

The supported trunk groups are from Trunk 1 to Trunk 8.

##### Type

The trunk mode set for this group may be “LACP” or “Static”. This field displays “-“ if no members are in the group.

##### Ports

The selected member ports in the group will be displayed in this column.

##### Link Status

This field displays the link state (Up or Down) for the specific port.

# Static Route

Static Route is the most basic routing method. Users have to manually-configure routing entries into routing table. Static Route is fixed and unchanged if the Network is changed. Static Route is good to be configured at a gateway of last resorts. The Network administrator has the full control over the static routing behavior, so the administrator must have enough background knowledge to handle it.

CONFIGURE IPV4 STATIC ROUTE INFORMATION

##### IP Address

Assign the IP Address to configure the static routing path.

##### Netmask

The Netmask is a number mapping to the Subnet Mask. For example, users configure the Netmask to 24 implies to configure the Subnet Mask to 255.255.255.0.

##### Next Hop

The Next Hop is an IP Address for a VLAN ID. The Next Hop implies the next node that the packet will be transferred to.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE IPV6 STATIC ROUTE INFORMATION

##### IPv6 Address

Assign the IPv6 Address to configure the static routing path.

##### Prefix

The Prefix defines the segment of the IPv6 address.

##### Next Hop

The Next Hop is an IPv6 Address for a VLAN ID. The Next Hop implies the next node that the packet will be transferred to.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

IPV4 STATIC ROUTE EXAMPLE

In the following diagram, we are going to configure a topology with Static Route for the system.

##### Configurations for SWA

- Configure VLAN for different subnets

Add VLAN 11 with untagged member port 5 and VLAN 12 with tagged member port 10 Configure PVID to 11 on port 5 because the end device (PC) has no ability to deal with the VLAN tag.

- Configure IP Address for different VLANs (Subnets)

The IP Address of VLAN 11 is 192.168.11.182 and the Subnet Mask is 255.255.255.0 The IP Address of VLAN 12 is 192.168.12.182 and the Subnet Mask is 255.255.255.0

- Configure Static Routing Rule

To connect to the internal LAN on SWB, users must configure the path on SWA

The Subnet of internal LAN on SWB is 192.168.13.0/24, and the IP Address of SWB’s external LAN is 192.168.12.166.

##### Configurations for SWB

- Configure VLAN for different subnets

Add VLAN 11 with untagged member port 5 and VLAN 12 with tagged member port 10 Configure PVID to 11 on port 5 because the end device (PC) has no ability to deal with the VLAN tag.

- Configure IP Address for different VLANs (Subnets)

The IP Address of VLAN 11 is 192.168.11.182 and the Subnet Mask is 255.255.255.0 The IP Address of VLAN 12 is 192.168.12.182 and the Subnet Mask is 255.255.255.0

- Configure Static Routing Rule

To connect to the internal LAN on SWA, users must configure the path on SWB

The Subnet of internal LAN on SWA is 192.168.11.0/24, and the IP Address of SWA’s external LAN is 192.168.12.182.

Note: Remember clicking “Apply” button to make the changes effective in each step.

# OSPFv2

Open Shortest Path First (OSPF) is one of the dynamic routing protocols and OSPFv2 is for IPv4 Networks. OSPF is the most widely used interior Gateway Protocol (IGP) and it is designed for medium-and-large-scale enterprise networks. OSPF nodes exchange neighbors’ information by Link-State and calculate the shortest path with their Cost to transmit packets. OSPF is operating under a hierarchical system and divide the system to several Areas by different Area IDs. OSPF nodes only exchange information with the nodes in the same Area.

CONFIGURE OSPFV2 INFORMATION

For more information, hover the mouse over the	icon in the system.

##### OSPF Mode

“Enable” or “Disable” OSPFv2 Function. The OSPFv2 function is default disabled. Please make sure the status of RIP is Disabled before Enable OSPFv2 function.

##### Networks

      - Network ID

The Networks ID implies the first IP Address of the subnet that will join the OSPF routing.

      - Prefix

The Prefix is a number mapping to the Subnet Mask. For example, users configure the Prefix to 24 implies to configure the Subnet Mask to 255.255.255.0.

The range of Prefix is from 0 to 32.

      - Area

The Area is an identity and only the nodes in the same area will exchange the OSPF information with each other. The Area 0 is a special area and called Backbone Area. All other areas must connect to the backbone area.

The range of Area is from 0 to 4294967295. : Click the plus icon to add an OSPF entry.

: Click the remove icon to delete the OSPF entry.

##### Router-ID

The Router-ID implies the identity for the working OSPFv2. The format of Router-ID is A.B.C.D.

##### Hello Interval

The Hello Interval is the period to send “Hello Message” to OSPF neighbors.

The range of Hello Interval is from 1 to 65535 second(s).

The default Hello Interval is 10 seconds.

##### Metric

The Metric is the total cost of the path from source device to destination device.

The range of Metric is from 1 to 65535.

The default Metric is 10.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

OSPFV2 STATUS

##### OSPF Mode

Display the state (“Enable” or “Disable”) of OSPF function.

##### Local IP

Display the information that configured on the localhost for OSPFv2.

##### Neighbor Information

Display the status of the neighborhood.

##### Neighbor IP

Display the information that learned from OSPF neighbors.

##### Hello Interval

Display the Hello Interval value of designated VLAN.

##### Metric

Display the Metric of designated VLAN.

OSPFV2 EXAMPLE

In the following diagram, we are going to configure a topology with Dynamic Routing – OSPFv2 for the system. Use the following commands or view OSPF Status page to check the link state after configurations are completed:

- show router ospf

- show router ospf neighbor

- show ip route

*Simulation Internet by through SWB.*

##### Configurations for SWA

- Configure VLAN for different subnets

Add VLAN 6 with tagged member port 9and VLAN 11 with untagged member port 5 Configure PVID to 11 on port 5 because the end device (PC) has no ability to deal with the VLAN tag.

- Configure IP Address for different VLANs (Subnets)

The IP Address of VLAN 6 is 192.168.6.182 and the Subnet Mask is 255.255.255.0 The IP Address of VLAN 11 is 192.168.11.182 and the Subnet Mask is 255.255.255.0

- Configure OSPF rules

Set Router ID to 0.0.0.1 for SWA

Configure subnet 192.168.6.0/24 to join OSPF network area 0

Configure subnet 192.168.11.0/24 to join OSPF network area 0

Enable OSPFv2 function on SWA

##### Configurations for SWB

- Configure VLAN for different subnets

Add VLAN 6 with tagged member port 9 and VLAN 7 with tagged member port 10 Both port 9 and port 10 are tagged members, so there is no need to configure PVID.

- Configure IP Address for different VLANs (Subnets)

The IP Address of VLAN 6 is 192.168.6.108 and the Subnet Mask is 255.255.255.0 The IP Address of VLAN 7 is 192.168.7.108 and the Subnet Mask is 255.255.255.0

- Configure OSPF rules

Set Router ID to 0.0.0.2 for SWB

Configure subnet 192.168.6.0/24 to join OSPF network area 0 Configure subnet 192.168.7.0/24 to join OSPF network area 0

Enable OSPFv2 function on SWB

##### Configurations for SWC

- Configure VLAN for different subnets

Add VLAN 7 with tagged member port 10 and VLAN 13 with untagged member port 5 Configure PVID to 13 on port 5 because the end device (PC) has no ability to deal with the VLAN tag.

- Configure IP Address for different VLANs (Subnets)

The IP Address of VLAN 7 is 192.168.7.166 and the Subnet Mask is 255.255.255.0 The IP Address of VLAN 13 is 192.168.13.166 and the Subnet Mask is 255.255.255.0

- Configure OSPF rules

Set Router ID to 0.0.0.3 for SWC

Configure subnet 192.168.7.0/24 to join OSPF network area 0 Configure subnet 192.168.13.0/24 to join OSPF network area 0

Enable OSPFv2 function on SWB

Note: Remember clicking “Apply” button to make the changes effective in each step.

# OSPFv3

Continued from previous chapter, OSPFv3 is an extension of OSPFv2 which can support both

IPv4 and IPv6 Networks.

There is no necessary to explicitly create a routing process for each subnet in OSPFv3. The routing process will be triggered by assigning an interface, which implies VLAN, to the OSPFv3 configurations. Users can configure several IPv6 address prefixes on a VLAN interface, so all prefixes on the VLAN interface will be included by default.

CONFIGURE OSPFV3 INFORMATION

For more information, hover the mouse over the	icon in the system.

##### OSPFv3 Mode

“Enable” or “Disable” OSPFv3 Function. The OSPFv3 function is default disabled. Please make sure the status of RIP is Disabled before Enable OSPFv3 function.

##### Networks

      - VLAN ID

Assign the designated VLAN interface to join OSPFv3 routing process.

      - Area

The Area is an identity and only the nodes in the same area will exchange the OSPF information with each other. The Area 0 is a special area and called Backbone Area. All other areas must connect to the backbone area.

The range of Area is from 0 to 4294967295. : Click the plus icon to add an OSPF entry.

: Click the remove icon to delete the OSPF entry.

##### Router-ID

The Router-ID implies the identity for the working OSPFv3. The format of Router-ID is A.B.C.D.

##### Hello Interval

The Hello Interval is the period to send “Hello Message” to OSPF neighbors.

The range of Hello Interval is from 1 to 65535 second(s).

The default Hello Interval is 10 seconds.

##### Metric

The Metric is the total cost of the path from source device to destination device.

The range of Metric is from 1 to 65535.

The default Metric is 10.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

OSPFV3 STATUS

##### OSPF Mode

Display the state (“Enable” or “Disable”) of OSPF function.

##### Local IPv6

Display the information that configured on the localhost for OSPFv3.

##### Neighbor Information

Display the status of the neighborhood.

##### Neighbor IPv6

Display the information that learned from OSPF neighbors.

##### Hello Interval

Display the Hello Interval value of designated VLAN.

##### Metric

Display the Metric of designated VLAN.

# RIPv1/v2

Routing Information Protocol (RIP) is another dynamic routing protocol for a small-scale Network. RIP uses Distance Vector to determine the routing path. The best path for RIP is the least hops during transmission. This is also the weakness of RIP because the path with least hops might not be the fastest path.

The RIP members broadcast their routing table to each other every 30 seconds to synchronize the Network and maintain the routing paths to be the least hops. The max number of hops that can be transferred between two nodes (routers) is 15. Therefore, the RIP function is only suitable for a small Network.

CONFIGURE RIPV1/V2 INFORMATION

For more information, hover the mouse over the	icon in the system.

##### RIP Mode

“Enable” or “Disable” RIP Function. The RIP function is default disabled.

Please make sure the status of OSPFv2 is Disabled before Enable RIP function.

##### Networks

      - Network ID

The Networks ID implies the first IP Address of the subnet that will join the RIP routing.

      - Prefix

The Prefix is a number mapping to the Subnet Mask. For example, users configure the Prefix to 24 implies to configure the Subnet Mask to 255.255.255.0.

The range of Prefix is from 0 to 32.

##### Version

Configure the Version of RIP. We support RIPv2 by default, but users can configure the version to support RIPv1.

    - Timers

      - Update Time

The Update Time is the interval to send broadcast for updating routing table with other routers in the same RIP Network.

The range of Update Time is from 5 to 2147483647.

The default Update Time is 30 seconds.

。 Timeout

The Timeout value is also called Aging Time. It will be count down from configured value until 0. If the system received a packet with the same RIP path, the Aging Time will be reset to the initial configured value and count down again. If the Aging Time is counting down to 0, the routing entry will be deleted from the routing table.

The range of Timeout is from 5 to 2147483647.

The default Timeout is 180 seconds.

。 Garbage

The Garbage-Collection Timer is used for a newly created routing path. When a new routing path is built, the timer creates and counts down. The routing path will be discarded if the timer is 0.

The range of Garbage is from 5 to 2147483647.

The default Garbage is 120 seconds.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

RIPV1/V2 STATUS

##### RIP Status

Display the state (“Enable” or “Disable”) of RIP function.

##### Local IP

Display the information that configured on the localhost for RIP.

##### Routing Network Information

Display the routing information that exchanges with other routers.

RIP EXAMPLE

In the following diagram, we are going to configure a topology with Dynamic Routing – RIP for the system. Use the following commands or view RIPv1/v2 Status page to check the link state after configurations are completed:

- show router rip status

- show router rip state

- show ip route

*Simulation Internet by through SWB.*

##### Configurations for SWA

- Configure VLAN for different subnets

Add VLAN 6 with tagged member port 9and VLAN 11 with untagged member port 5 Configure PVID to 11 on port 5 because the end device (PC) has no ability to deal with the VLAN tag.

- Configure IP Address for different VLANs (Subnets)

The IP Address of VLAN 6 is 192.168.6.182 and the Subnet Mask is 255.255.255.0 The IP Address of VLAN 11 is 192.168.11.182 and the Subnet Mask is 255.255.255.0

- Configure RIP rules

Configure subnet 192.168.6.0/24 to join RIP network Configure subnet 192.168.11.0/24 to join RIP network

Enable RIP function on SWA, the default RIP is running version 2.

##### Configurations for SWB

- Configure VLAN for different subnets

Add VLAN 6 with tagged member port 9 and VLAN 7 with tagged member port 10 Both port 9 and port 10 are tagged members, so there is no need to configure PVID.

- Configure IP Address for different VLANs (Subnets)

The IP Address of VLAN 6 is 192.168.6.108 and the Subnet Mask is 255.255.255.0 The IP Address of VLAN 7 is 192.168.7.108 and the Subnet Mask is 255.255.255.0

- Configure RIP rules

Configure subnet 192.168.6.0/24 to join RIP network Configure subnet 192.168.7.0/24 to join RIP network

Enable RIP function on SWB, the default RIP is running version 2.

##### Configurations for SWC

- Configure VLAN for different subnets

Add VLAN 7 with tagged member port 10 and VLAN 13 with untagged member port 5 Configure PVID to 13 on port 5 because the end device (PC) has no ability to deal with the VLAN tag.

- Configure IP Address for different VLANs (Subnets)

The IP Address of VLAN 7 is 192.168.7.166 and the Subnet Mask is 255.255.255.0 The IP Address of VLAN 13 is 192.168.13.166 and the Subnet Mask is 255.255.255.0

- Configure RIP rules

Configure subnet 192.168.7.0/24 to join RIP network Configure subnet 192.168.13.0/24 to join RIP network

Enable RIP function on SWC, the default RIP is running version 2.

Note: Remember clicking “Apply” button to make the changes effective in each step.

# RIPng

RIP next generation (RIPng) is an extension of RIPv2 to support IPv6. The following are the differences between RIPng and RIPv2. Although RIPng is the next generation of RIPv2, the RIPng does not support RIPv1. The operation of RIPng is to assign a set of route entries into a specific next-hop rather than record next-hops for each route entry on RIPv2. The multicast group of RIPng is FF02::9 but for RIPv2, it uses 224.0.0.9.

The max number of hops that can be transferred between two nodes is also 15 for RIPng. It is a

limitation for using on a large-scale network topology.

#### CONFIGURE RIPNG INFORMATION

For more information, hover the mouse over the	icon in the system.

##### RIP Mode

“Enable” or “Disable” RIPng Function. The RIP function is default disabled.

Please make sure the status of OSPF is Disabled before Enable RIPng function.

##### Networks

      - VLAN ID

The VLAN ID implies the VLAN interface that will join the RIP routing.

    - Timers

      - Update Time

The Update Time is the interval to send broadcast for updating routing table with other routers in the same RIP Network.

The range of Update Time is from 5 to 2147483647.

The default Update Time is 30 seconds.

。 Timeout

The Timeout value is also called Aging Time. It will be count down from configured value until 0. If the system received a packet with the same RIP path, the Aging Time will be reset to the initial configured value and count down again. If the Aging Time is counting down to 0, the routing entry will be deleted from the routing table.

The range of Timeout is from 5 to 2147483647.

The default Timeout is 180 seconds.

。 Garbage

The Garbage-Collection Timer is used for a newly created routing path. When a new routing path is built, the timer creates and counts down. The routing path will be discarded if the timer is 0.

The range of Garbage is from 5 to 2147483647.

The default Garbage is 120 seconds.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

RIPNG STATUS

##### RIPng Status

Display the state (“Enable” or “Disable”) of RIPng function.

##### Local IPv6

Display the information that configured on the localhost for RIPng.

##### Routing Network Information

Display the routing information that exchanges with other routers.

# VRRP

Virtual Router Redundancy Protocol (VRRP) is a function to avoid single point of failure in the static default routed environment. There are two or more routers in a VRRP group to backup each other. They share the same virtual IP address in the Network and one of them called Master provides routing services for other devices. Others in the same VRRP group are Backup routers. When the Master router is broken, the Backup routers will replace the original Master router based on their Priority value. The router with the highest Priority value will be the next Master, so that the routing can be uninterrupted.

CONFIGURE VRRP INFORMATION

For more information, hover the mouse over the	icon in the system.

##### VLAN ID

Display the current VLAN ID that is configured with members and IP Address.

##### Group ID

The Group ID is the identity for the VRRP Group. All routers in the same VRRP group MUST be configured with the same Group ID.

The range of Group ID is from 1 to 255

##### Adv. Timer

The timer is the period to send Advertisement to make sure the Master is still alive. The Master route will be changed if other Backup routers miss Advertisement message after the timer expired to make sure the continuous services.

The range of Adv. Timer is from 1 to 60 seconds

##### Priority

The Priority is used to decide the Master in the VRRP group.

The range of Priority is from 1 to 254

Note: the higher the value the higher the priority

##### Virtual IP Address

The Virtual IP Address is a public IP Address in the Network. All routers in the same VRRP group are configured with the same Virtual IP Address.

Note: The Virtual IP Address must be configured different from VLAN IP Addresses.

##### Preempt

“Enable” or “Disable” Preempt Mode. When the Preempt Mode is disabled, other VRRP routers are not allowed to preempt the Master role.

##### Mode

“Enable” or “Disable” VRRP function on this VLAN.

Note: Users must configure all VRRP parameters before enable VRRP function.

##### State

There are four states for the VRRP

Master: This is a major router that provides services in the VRRP group.

Backup: This is a backup router in the VRRP group. When the VRRP Master is broken, the backup router will provide services.

Init: VRRP function is under initialization. NULL: VRRP function is disabled.

VRRP EXAMPLE

In the following diagram, we are going to configure a topology with VRRP for router backup.

##### Configurations for SWA

- Configure VLAN 7 on SWA for VRRP interface and assign IP Address to the VLAN

- Configure VRRP information for SWA (Master Router)

Set Group ID to 1, Advertisement Timer to 10 seconds, Priority to 100, and Virtual IP Address to 10.10.10.5. Make sure the Mode is configured to “Enable”.

##### Configurations for SWB

- Configure VLAN 7 on SWB for VRRP interface and assign IP Address to the VLAN

- Configure VRRP information for SWB (Backup Router)

Set Group ID to 1, Advertisement Timer to 10 seconds, Priority to 50, and Virtual IP Address to 10.10.10.5. Make sure the Mode is configured to “Enable”.

Because SWB is the Backup Router, the Priority value must be below the Priority value of SWA.

Note: The Group ID and Virtual IP Address should be the same on all VRRP members. Note: Remember clicking “Apply” button to make the changes effective in each step.

# Storm Control

A traffic storm happens when there is excessive packets flood to the LAN and decreases the performance. The Storm Control function is used to prevent the system from breaking down by the broadcast, multicast, or unknown unicast traffic storm. When the Storm Control is enabled on the specific traffic type, the system will monitor the incoming traffic. If the traffic is more than the configured level, the traffic will be dropped to avoid the storm.

#### CONFIGURE STORM CONTROL INFORMATION

##### Traffic Type

Three types of traffics are supported in the Storm Control: Broadcast, Multicast, and

Unknown Unicast.

    - Mode

“Enable” or “Disable” Storm Control function in the specific traffic type.

##### Level

Three frame levels are available: High, Middle, and Low. If the frames of specific traffic type are more than the set level, the system will drop the type of frames to prevent the system from breaking down.

High: More than 2500 frame per second.

Mid: More than 1000 frame per second.

Low: More than 500 frame per second.

           (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# 802.1X Settings

802.1X is an IEEE standard defined Port-based Network Access Control. It provides a more secured authentication mechanism for the devices, which would like to connect to a LAN or a WAN. The Port-based Network Access Control protocol is a convenient method for the users because the authentication is per-port and once the port passes the authentication, it is not required to authenticate again when changing to another device, i.e., without security. Therefore, MAC-based access control is provided. It is a more secure, but less convenient method for authentication. Only the device with the MAC Address that has passed the authentication can be added to the networks. These two methods are optional on each port and the users can select one of them on different ports.

CONFIGURE 802.1X BASIC INFORMATION

For more information, hover the mouse over the icon in the system.

##### Basic Settings

      - 802.1X Mode

“Enable” or “Disable” 802.1X function on the switch.

      - Server Type

Select the 802.1X server type to “Local Database” or “RADIUS Server”.

Local Database: The database is maintained in a table stored in the switch. The client must send the username and password to authenticate with the switch’s database.

RADIUS Server: The database is maintained in other devices running RADIUS service. The authentication follows the RADIUS protocol including communication and encryption.

CONFIGURE 802.1X PORT INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Port Settings

      - Port

Port1 to PortN, where N is based on the total port number.

      - Enable

“Enable” or “Disable” 802.1X function on the port. “Yes” means 802.1X is enabled on the port and the port is locked until it passes the authentication.

      - Mode

Select the 802.1X mode to “Mac-based” or “Port-based”.

Mac-based: Only the MAC Address, which passed the authentication can connect to the networks.

Port-based: If the port had passed the authentication, every device connected to the port can connect to the networks.

- Re-Auth

“Enable” or “Disable” re-authentication on the port. “Yes” means re-authentication is enabled on the port and the port must re-authenticate with the server every re-auth period.

- Re-Auth Period

This is a time interval, which is used in re-authenticating the server.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE LOCAL DATABASE INFORMATION

For more information, hover the mouse over the icon in the system.

##### User Name

The User Name is used in authentication.

The max. length for the User Name is 32 characters. Note: #, \, ', ", ? are invalid characters.

##### Password

The Password is used in authentication.

The max. length for the Password is 20 characters. Note: #, \, ', ", ? are invalid characters.

##### Confirm Password

The Confirm Password field must be the same as Password field.

	: Click the plus icon to add a Username/Password row.

	: Click the remove icon to delete the Username/Password row.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE RADIUS SERVER INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Server IP

The Server IP is the IP address of the server.

##### Service Port

The Service Port is the listening port on the RADIUS server.

##### Shared Key

The key is used in establishing the connection between the server and the authenticator before authentication.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Service Control

We provide 5 types of interface which are HTTP, HTTPS, SSH, Telnet, and Console Port  to access the management interface of the switch. Users can configure the authority for each type of service to be enabled or disabled. Reset Button is another method to reboot or reset factory default. We also provide the configuration for the Reset Button to enable or disable its function. All the services are enabled by default and users can disable unused service to make the system more secure.

#### CONFIGURE SERVICE CONTROL INFORMATION

##### HTTP

Enable or Disable to access management interface by HTTP which is the foundation of data communication for the World Wide Web (WWW).

##### HTTPS

Enable or Disable to access management interface by HTTPS which is an adaptation of HTTP for security. The communication will be encrypted in HTTPS.

##### SSH

Enable or Disable to access management interface by SSH, which is a cryptographic network protocol. SSH provides a secure channel over an unsecured network in the client-server architecture. The switch plays the role of SSH server and hosts plays the role of SSH client.

##### Telnet

Enable or Disable to access management interface by Telnet which is a text-oriented virtual terminal connection. It is less secure than SSH because it does not encrypt any data even password when the data is transmitting.

##### Console

Enable or Disable to access management interface by Serial Console Port. Disable the Console Port can avoid the misconfiguration by someone who can access the device on-site.

##### Reset Button

Enable or Disable to react when users press the Reset Button. The Reset Button provides different functions including reboot and reset factory default. Disable Reset Button is a protection from mistaking the button to reboot the system or restore the system to default state.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Access Control List

An access control list provides rules to apply all network ports. The inbound traffic checked the entries in the ACL table. Each entry can be the MAC entry for layer 2 address and IP entry for the

layer 3 address. And it can check the source address or destination address. User can adjust the address mask to provide the group setting in one entry. Entry have two actions that can permit or deny network packet transmitting to another port.

#### CONFIGURE ACCESS CONTROL LIST

##### Index

Entry number in the ACL table. Traffic packet will be checked with the index sequence.

The range of the Index is from VLAN 1 to 128

##### Action

Drop: Packet will be discarded if it hit the address rule.

Permit: Packet will be forwarded if it hit the address rule.

##### Address Type

Src: Address rule bases on the source address

Dst: Address rule bases on the destination address

##### Address

MAC address with byte colon format. For example: 00:80:C2:01:23:45 IP Address with decimal dot format. For example: 192.168.1.123

##### Address Mask

Bit mask for MAC address with byte colon. Bit 1 is checking in rule. Otherwise bit 0 is exclude in checking rule.

Subnet mask for IP address with decimal dot. To decide the type of network.

#### ACCESS CONTROL LIST EXAMPLE

Configure Permission by MAC Address

- Login Command Line Interface (CLI) with username and password which are admin/admin by default.

- Configure ACL rule for the MAC Address of Admin’s PC by issuing:

acl mac 1 permit src 68:02:35:FF:AB:01 ff:ff:ff:ff:ff:ff

Note: the index ID is from 1 to 128

Configure Permission by IP Address

- Login Command Line Interface (CLI) with username and password which are admin/admin by default.

- Configure ACL rule for the IP Address of Admin’s PC by issuing:

acl ip 1 permit src 192.168.1.99 255.255.255.0

Note: the index ID is from 1 to 128

Configure Deny by MAC Address

- Login Command Line Interface (CLI) with username and password which are admin/admin by default.

- Configure ACL rule for the MAC Address of Visitor’s PC by issuing:

acl mac 1 drop src 68:02:35:FF:CD:01 ff:ff:ff:ff:ff:ff

Note: the index ID is from 1 to 128

Configure Deny by IP Address

- Login Command Line Interface (CLI) with username and password which are admin/admin by default.

- Configure ACL rule for the IP Address of Visitor’s PC by issuing:

acl ip 1 drop src 192.168.1.102 255.255.255.0

Note: the index ID is from 1 to 128

# SSH

To reduce the steps for login the system via SSH connection, the public/private key pair is a good choice for users. The pair of keys is created on the local device and users must provide the public key to the target device, for example, the Ethernet switch. When users connect to the target device, the system creates a safe connection by SSH. The localhost and target device authenticates each other with the public and private keys to make sure the security.

#### BACKUP HOST KEY FILE

##### Backup to Localhost

      - File Name

Specify the File Name for the SSH Host Key file, which will be saved to the localhost.

##### Backup to USB

Ensure there is a USB stick inserted into the USB port.

      - Backup Host Key File

Specify the File Name for the saved SSH Host Key file, which will be saved to the USB.

Note: The file system of USB must be FAT32.

	   (Save Button)

Click the "Save" button to save the configuration file to the Localhost or USB.

#### RESTORE HOST KEY FILE

##### Restore from Localhost

      - File Name

Select the SSH Host Key file, which is saved in the Localhost.

##### Restore from USB

Please ensure there is a USB stick inserted into the USB port.

      - File Name in USB

The File Name of the saved SSH Host Key file, which is saved to the USB. If the configuration file is saved in the directory, please specify the full path.

Note: The file system of USB must be FAT32.

	  (Restore Button)

Click the "Restore" button to restore the SSH Host Key from the Localhost or USB.

#### HOST KEY INFORMATION

The current SSH Host Key is displayed in the “SSH Host Key” page. The system only accept one SSH Host Key, once users restore another Host Key, the current Host Key will be replaced.

# Port Mirroring

Port Mirroring is a feature that copies the incoming or outgoing packets on one or more ports to another destination port. It is particularly useful to monitor the network traffic and analyze the copied traffic. Port Mirroring helps network management to keep a close eye on the network and debug when some issues arise.

#### CONFIGURE PORT MIRRORING INFORMATION

##### Mirroring Mode

“Enable” or “Disable” the Port Mirroring function. If the user enables Port Mirroring function, the system will transmit the traffic of the specific “Sniffer Mode” from “Source Port” to “Destination Port”.

##### Source Port

The traffic on the Source Ports will be sniffed to the Destination Port.

##### Sniffer Mode

Both Tx and Rx: Sniffs both transmitting and receiving traffics. Tx Only: Sniffs only the transmitting traffic.

Rx Only: Sniffs only the receiving traffic.

##### Destination Port

The traffic will sniff to the Destination Port. This port is usually connected to a host running the software to observe the packets.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Ping

Ping is a tool used to test the reachability of a device on the IP network. Ping is enabled by sending Internet Control Message Protocol (ICMP) request to the target device and waits for the response packet from the target device to check the connection.

PING ANOTHER DEVICE WITH IPV4/IPV6

##### Type

For more information, hover the mouse over the	icon in the system.

Ping a connected device with “IPv4” or “IPv6” protocol.

##### IP Address

The IP address of the connected device is verified based on the type.

##### Count

Sets the count times. The system will send “Count” number ICMP packets to the specific IP address and wait for the response.

The range of the Count is from 3 to 50. The default Count is 3.

##### Result

The result of the ping shows the response from the specific IP address. If the specific IP address does not respond, it displays No Response.

##### “Start” Button

Click the “Start” Button to start the ping to the IP address.

##### “Stop” Button

Click the “Stop” Button to stop the ping to the IP address before the count is completed.

##### “Clear” Button

Click the “Clear” Button to clear the “Result”.

##### “Reset” Button

Click the “Reset” Button to clear the “Result” and reset the “IP Address” and “Count”

number.

# Cable Diagnostic

This command can check the status of copper cables with the time domain reflectometer (TDR) technology. It can detect a cable fault by sending a detect signal and read the reflecting back. With this test, it can help to identify and narrow down the physical level issue.

#### DISPLAY CABLE DIAGNOSTIC

##### Port Selector

Select the port number to test.

Port 1 to N, where N is based on the total port number.

##### Cable status

The status of cable. It contains the number of pairs in the cable and the error amount.

Usually there are 4 pair in the CAT-5E cable for Gigabit Ethernet link.

##### Pair status

The status of each pair of port. ‘Ok’ status means cable is connected to another node. ‘Open’

status means cable does not connect to any device.

##### Length

The length of each pair of port in meters. Please note the error amount is around 10 meters due to the TDR technology. The short cable less than the error amount might be untastable.

# LLDP

LLDP is Link Layer Discovery Protocol, and it is a vendor-neutral layer 2 protocol that is defined by IEEE 802.1AB. LLDP is used in advertising identity of the devices, capabilities and neighbors on the LAN. The information from the neighbors enables the switch to quickly identify the devices and interoperate with each other more smoothly and efficiently. The neighbor table shows the information about the device that is next to the port. The LLDP can only get information from the device that is close to it. If the users want to know the topology of the LAN, they can collect all information from the device and analysis the neighbor table.

CONFIGURE LLDP INFORMATION

For more information, hover the mouse over the	icon in the system.

##### LLDP Mode

“Enable” or “Disable” the LLDP function.

##### LLDP Timer

The LLDP Timer is a time interval to send LLDP messages. The range of the LLDP Timer is from 5 to 32767 seconds. The default LLDP Timer is 30 seconds.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

LLDP NEIGHBOR TABLE

##### Local Port

The port connected to the LLDP neighbor on the local switch.

##### Remote System Name

This is the system name of the LLDP neighbor. This value is set and provided by the remote device.

##### Chassis ID

The Chassis ID defines the MAC Address of the LLDP neighbor.

##### Remote Port

This field displays the port information received from the LLDP neighbor.

##### Port ID

The Port ID displays the port identity of the connected port on the LLDP neighbor.

##### Address

The Address displays the IP address of the LLDP neighbor.

# System Warning

System Warning contains “System Event Log”, “SMTP Settings”, and “Event Selection” for different types of services such as “Fault Alarm”, “System Log”, “SMTP”, and “SNMP Trap”. These logs are extremely useful for the administrator to manage and debug the system. When the system is powered off or when someone tries to login the system or the system reboots abnormally, or when some of the interfaces are linked down, the system sends log messages to notify specific users and record the events on the server or assigned platform. Users can also connect an alarm buzzer to the relay alarm pins. When the configured “Fault Alarm” events are triggered, the alarm buzzer will ring to notify the users.

#### CONFIGURE SYSTEM WARNING INFORMATION

For more information, hover the mouse over the	icon in the system.

##### System Log Mode

    - Select the checkbox to send system log to Local (Switch), Remote, or USB when events happened.

##### Remote Server IP Address

The field contains the IP Address of the remote server. If the “Remote” mode is enabled, users must assign this IP Address to receive the system logs. The system supports both IPv4 and IPv6 addresses for the remote server.

##### Service Port

The port is used to listen to the system log packets on the remote server.

The range of the Service Port is from 1 to 65535. The default Service Port is 514.

           (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

#### SYSTEM EVENT LOG

##### Log Text Area

The system event information displays if the “Local” system log mode is enabled, and the configured events are triggered.

	   (Clear Button)

Click the “Clear” button to clear the system event log in the text area.

	  (Refresh Button)

Click the “Refresh” button to refresh the system event log in the text area.

CONFIGURE SMTP INFORMATION

For more information, hover the mouse over the	icon in the system.

##### Server Settings

      - SMTP Status

“Enable” or “Disable” the SMTP function.

      - Server Address

This is the IP address or URL of the SMTP Server. For example, the SMTP server address provided by Google is “smtp.gmail.com”.

      - Server Port

This field is the port listening on the server for the SMTP request. For security, we suggest users configure the server port to 465 for SSL or 587 for TLS.

The range of the Service Port is from 1 to 65535.

The default Service Port is 25. Port 25 is the default port for e-mail server.

- Sender E-mail

The Sender E-mail is the e-mail address used to send the notifications to Recipients.

- Mail Subject

The Mail Subject is a string that is displayed in the E-mail title.

Note: #, \, ', ", ? are invalid characters.

- SMTP Authentication

“Enable” or “Disable” to authenticate the SMTP server with the configured username and password.

- User Name

The username is used in authentication with the SMTP server.

The max. length for the User Name is 32 characters. Note: #, \, ', ", ? are invalid characters.

- Password

The password is used in authentication with the SMTP server.

The max. length for the Password is 32 characters. Note: #, \, ', ", ? are invalid characters.

##### Recipient Settings

      - E-mail Address 1-4

The configured e-mail address will receive the notifications if the SMTP is enabled, and the events set on “Event Selection” are triggered.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

#### CONFIGURE SYSTEM EVENT SELECTIONS

##### Event

There are 5 events on the System Events.

Authentication Failure: Login failed on the web console or CLI. It may be caused due to incorrect username or password.

ERPS Change: The ERPS function is working, and the topology is changed. Power 1 - 4: The power 1 to 4 is powered off.

Cold Start: The system reboots due to interruption of power supply.

Warm Start: The system reboots by issuing “reboot” command on CLI or clicking the “reboot icon” on the web console.

Digital Input: The signal from the digital input is changed from high to low or low to high.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

#### CONFIGURE INTERFACE EVENT SELECTIONS

##### Event

The events on the “Interface Events” display the link status for each port. Fault Alarm is triggered only during link down and other system log types of support both link up and link down.

##### Fault Alarm

The Fault LED will turn on red and relay will turn ON, if the configured events are triggered. By default, the Fault LED is green, and relay is turned OFF in the normal situation,

##### System Log

When the configured events are triggered, the logs will be displayed in the “System Event Log” page, remote server, or saved to a USB file named “message”. This is based on the settings of the “System Log Mode” in the “System Log Settings” page.

Note: The file system of USB must be FAT32.

##### SMTP

If the SMTP is enabled and the configured events are triggered, the system will send an e-mail notification to the e-mail addresses of the assigned recipient set in the “SNMP Settings” page.

##### SNMP

If the SNMP Trap is enabled and the configured events are triggered, the system will send event information to the assigned “Trap Receiver IP”, which is set in the “SNMP Trap” page.

           (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE SFP DDM EVENT SELECTIONS

##### Event

There are 5 events on the “SFP DDM Events”: Current, Rx Power, Tx Power, Temperature, and Voltage. Enable or Disable the event fault alarm or system warning when the value is higher than the high alarm/warning threshold or the value is lower than the low alarm/warning threshold.

# Data Collection

The health of switch system is especially important in the real application. For most switches, they provide basic real-time traffic and PoE status, but users need the long-term records to analyze and statistic for the system. For this purpose, we implement the Data Collection function to collect traffic and PoE status periodically and save the collected data to the USB device. In addition to this, we also provide charts to display the collected data. Users can easily recognize the situation of the switch system and find the unusual points from the charts.

To ensure the accuracy of the data, the NTP service must be turned on before enable Data Collect function, so that when users find an abnormal record, they can trace it by the recording time. And there is no worry for the size of system storage because the data is saved in the USB. The data even can be move to other devices to display or users can use the collected raw data to do other application.

#### CONFIGURE DATA COLLECTION SETTINGS

USB and NTP are essential before users enable the Data Collection functions. Please check if there is an USB inserted and the NTP service is also enabled. The file system of USB must be FAT32.

##### Collection

“Enable” or “Disable” Data Collection Function on the switch. The Traffic and PoE Data Collection can be enabled only when the Collection is enabled.

    - PoE Data Collection (PoE Models Only)

“Enable” or “Disable” PoE Data Collection function on the switch.

##### Traffic Data Collection

“Enable” or “Disable” Traffic Data Collection function on the switch.

#### RESET COLLECTED DATA

##### Port

Port 1 to Port N, N is based on the total port number.

##### Traffic

Check the checkbox to reset the data for the designated port. After reset, the collected data will be removed from the USB.

Note: It cannot undo after reset, please make sure you want to reset the file.

    - PoE (PoE Models Only)

Port 1 to Port N, N is based on the total port number.

POE STATUS CHARTS (PoE Models Only)

For more information, hover the mouse over the	icon in the system.

##### Port (Drop-down Selector)

Port1 to PortN, where N is based on the total PoE port number. The PoE Status Chart is displayed by port.

##### Total Data Interval

The interval is the date time from first data to last data that collected in the USB.

##### Current Data Interval

The interval is the date time from first data to last data that displayed on the current chart.

##### Data Interval (Drop-down Selector)

Select an interval to search data. The returned data will be displayed on the chart. The number of data is limited by the system, if the selected interval is larger than the limitation, the system will return an acceptable interval (Shown as the following screenshot).

Note: After configuring “Data Interval”, click "Search" button to get data in the interval.

##### Chart

The chart displays both watts (blue line) and voltage (green line) data.

##### Refresh Chart (Button)

Press the Refresh Chart button to refresh the chart and get the updated data.

##### Data Collect Rate

The field is the period to collect data. The system will get the real-time data periodically according to the configured Data Collect Rate.

Note: PoE Status Charts and Interface Traffic Charts are shared the same Data Collect Rate.

The range of the Data Collect Rate is from 60 to 600 seconds. The default Data Collect Rate is 180 seconds.

Note: After configuring “Data Collect Rate”, click "Apply" button to make the changes effective.

#### INTERFACE TRAFFIC CHARTS

For more information, hover the mouse over the	icon in the system.

##### Port (Drop-down Selector)

Port1 to PortN, where N is based on the total switch port number. The Interface Traffic Chart is displayed by port.

##### Total Data Interval

The interval is the date time from first data to last data that collected in the USB.

##### Current Data Interval

The interval is the date time from first data to last data that displayed on the current chart.

##### Data Interval (Drop-down Selector)

Select an interval to search data. The returned data will be displayed on the chart. The number of data is limited by the system, if the selected interval is larger than the limitation, the system will return an acceptable interval (Shown as the following screenshot).

Note: After configuring “Data Interval”, click "Search" button to get data in the interval.

##### Chart

The chart displays transmitted bytes (blue line) and received bytes (green line) data.

##### Refresh Chart (Button)

Press the Refresh Chart button to refresh the chart and get the updated data.

##### Data Collect Rate

The field is the period to collect data. The system will get the real-time data periodically according to the configured Data Collect Rate.

Note: Interface Traffic Charts and PoE Status Charts are shared the same Data Collect Rate.

The range of the Data Collect Rate is from 60 to 600 seconds. The default Data Collect Rate is 180 seconds.

Note: After configuring “Data Collect Rate”, click "Apply" button to make the changes effective.

# MAC Table

MAC address is Media Access Control address, which is used in layer 2 switching. A MAC Address table is maintained by the switch to transmit frames more efficiently. When the switch receives a frame, the system will check the MAC table and forward the frame to the corresponding port. The MAC Address table is built dynamically by the received frames and when the system receives a frame with an unknown MAC address, it floods the frame to all LAN ports in the same VLAN. When the destination device replies the system identifies the MAC Address and the target port.

The MAC Address for the switch is designed as per-port-per-MAC, which implies each port has its own MAC Address. This is for MAC sensitive protocols such as Spanning-tree protocol. The MAC Address display on the right side of WEB GUI is the MAC Address for whole system and the MAC Addresses for the ports are increasing by 1 from port 1 to last port.

For example, the MAC Address of the system is 68:02:35:FF:FF:05, and there are 8-port on the switch. The MAC Address for each port will be:

| Port | MAC Address | Port | MAC Address |
| --- | --- | --- | --- |
| Port 1 | 68:02:35:FF:FF:06 | Port 5 | 68:02:35:FF:FF:0A |
| Port 2 | 68:02:35:FF:FF:07 | Port 6 | 68:02:35:FF:FF:0B |
| Port 3 | 68:02:35:FF:FF:08 | Port 7 | 68:02:35:FF:FF:0C |
| Port 4 | 68:02:35:FF:FF:09 | Port 8 | 68:02:35:FF:FF:0D |

Note: The MAC Address is hex format, so the number after “09” is “0A”.

#### CONFIGURE STATIC MAC ADDRESS INFORMATION

##### VID

For more information, hover the mouse over the	icon in the system.

The VID is the VLAN group ID, which contains the configured MAC Address .

The range of the VID is from 1 to 4094.

##### MAC Address

This field is the static MAC Address of the configured member ports in the VLAN group.

##### Group Member

The Group Member is the port(s) in the VLAN group, to which the configured MAC Address belongs.

	: Click the plus icon to add a static MAC Address row.

	: Click the remove icon to delete the static MAC Address row.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

MAC ADDRESS TABLE

##### VID

The VID is the VLAN group ID, which contains the configured MAC Address.

##### MAC Address

The MAC Address column displays the learnt or configured MAC Addresses.

##### Type

The Type column displays the type (Learning or Static) of the MAC Address. Learning: The MAC address is learnt from the transmitting frames.

Static: The MAC Address is configured by the users or the system.

##### Source

The Source column displays the port(s) to which the MAC Address belong.

# Authorization

The "Username" and "Password" are important information both in the "Command Line Interface" or "Web Console". Users have to login into the system before doing any configuration. We strongly suggest the users to change at least the password for security when they are going to use this device.

We also provide authentication with RADIUS/TACACS+ server from software version 1.0.3. Users can maintain the login information in their own RADIUS/TACACS+ database and allow several usernames/passwords to login the system.

#### CONFIGURE LOGIN INFORMATION

##### Mode

For more information, hover the mouse over the	icon in the system.

There are three modes for login authentication.

Local: The username and password are defined in the system. Currently we support two-level users – Admin and Read-only user. The Admin can access any page and configure the system but the read-only user can only access status pages.

Radius: The username and password are defined in the RADIUS server and when user’s login the system, the system will authenticate with the RADIUS server to get the login permission. The password will be encrypted during the transmitting.

Tacacs+: The username and password are defined in the TACACS+ server and when users login the system, the system will authenticate with the TACACS+ server to get the login permission. The whole payload and password will be encrypted during the transmitting.

##### Username

The account used to login to the system.

The maximum length of the Username is 32 characters Only alphabet (A-Z, a-z) and numbers (0-9) are allowed. The default Username is admin.

##### Password

The password used to login to the system. We provide password strength bar for reference. There are 3 levels - Weak, OK, and Great. We strongly recommend users configuring the password to “Great” level for security.

The maximum length of the Password is 32 characters.

Only alphabet (A-Z, a-z), numbers (0-9), and chars (!,@,%,^,*,(,)) are allowed. The default Password is admin.

##### Confirm Password

It is used to confirm the value specified by the users in the "Password" field. The value of the field must be the same as "Password".

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE RADIUS SERVER INFORMATION

This section only display when the mode in the Basic Settings is set to “Radius”.

For more information, hover the mouse over the	icon in the system.

##### Server IP

The IP address of the RADIUS server must in the same subnet as the IP address of the switch.

##### Server Port

The port is listening to the RADIUS service on the RADIUS server. The range of the Server Port is from 1 to 65535.

The default Server Port is 1812.

##### Shared Key

The Shared Key is a string that used to build the connection with the RADIUS server. It must be the same as the string/secret set in the RADIUS server.

The maximum length of the Shared Key is 32 characters.

##### Retransmit Times

The password used to login to the system.

The range of the Retransmit Times is from 1 to 1000.

##### Timeout

The time interval is used to waiting for the response from the RADIUS server. The range of the Timeout is from 1 to 1000 seconds.

The default Timeout is 5 seconds.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

CONFIGURE TACACS+ SERVER INFORMATION

This section only display when the mode in the Basic Settings is set to “Tacacs+”.

For more information, hover the mouse over the	icon in the system.

##### Server IP

The IP address of the TACSCS+ server must in the same subnet as the IP address of the switch. The system supports both IPv4 and IPv6 addresses for the TACACS+ server.

##### Server Port

The port is listening to the TACSCS+ service on the TACSCS+ server. The range of the Server Port is from 1 to 65535.

The default Server Port is 49.

##### Shared Key

The Shared Key is a string that used to build the connection with the TACSCS+ server. It must be the same as the string/secret set in the TACSCS+ server.

The maximum length of the Shared Key is 32 characters.

##### Timeout

The time interval is used to waiting for the response from the TACSCS+ server. The range of the Timeout is from 1 to 1000 seconds.

The default Timeout is 30 seconds.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# Firmware Upgrade

For a better performance and wider industrial applications, we constantly develop new features and revise the issues from the users. We suggest the users to upgrade the system to the newest firmware version to have a better user experience.

We provide 2 ways to upgrade the firmware from the Web Console, - one is saving the firmware file in the USB stick and another one is saving the firmware file on the PC. If the firmware file is on the PC, the users will have to only select the file and click Apply button, for the system to upgrade it automatically.

#### UPGRADE FIRMWARE VERSION - UPLOAD FIRMWARE FILE

##### Firmware Image

Click the "Select File" button to select the firmware image provided by the sales or support. The Firmware Version displayed on the system can be customized by the file name. For example, if you want the version to be called as 1.2.3, you only need to modify the file name to XXX-v1.2.3 (XXX is the original file name).

##### Selected File

After selecting a firmware image to be uploaded, the selected file name will be displayed in this field.

	   (Upload Button)

After selecting the firmware image, click "Upload" button to upload it.

#### UPGRADE FIRMWARE PROCESS - UPLOADING FIRMWARE FILE

The following steps are performed when the system starts to upgrade after the "Apply" button is clicked:

- Uploading the firmware image

The progress bar displays the uploading percentage.

- Verifying the uploaded file

When the file is 100% uploaded, the system starts to verify the uploaded file to make sure it is valid. By default, the firmware image is encrypted to prevent the attack on man-in-the-middle. Optionally, higher encryption methodology is also provided.

- Installing the uploaded firmware image

The new firmware will install after the system validates it.

- Rebooting the system

The system will reboot automatically if the firmware is upgraded without any issue. The progress bar displays the rebooting progress.

UPGRADE FIRMWARE VERSION - COPY FIRMWARE FILE FROM USB

##### Image File Name

Enter the name of the firmware image in the USB. The system will try to identify the file with specified file name to upload it to the system.

Note: The file system of USB must be FAT32.

	   (Upload Button)

After entering the firmware image name, click "Upload" button to copy it from the USB to the system.

UPGRADE FIRMWARE PROCESS - COPY FIRMWARE FILE FROM USB

- Copying the firmware image from USB to switch

The system will also check if the USB is inserted, and file exists.

- Verifying the uploaded file

After copying the firmware file to switch, the system starts to verify the uploaded file to make sure it is valid. By default, the firmware image is encrypted to prevent the attack on man-in-the-middle. Optionally, higher encryption methodology is also provided.

- Installing the uploaded firmware image

The new firmware will install after the system makes sure it is valid.

- Rebooting the system

The system will reboot automatically if the firmware is upgraded without any issue. The progress bar displays the rebooting progress.

# Config Backup

In the normal application, there are several switches in the Network, and they might be configured to the same features. To facilitate this, the users can configure one of the switches and save the configuration file to localhost (for example: users' PC) or USB sticks and then restore the configurations on another switch via "Config Restore" function. Configuration file in the USB can also have a way to fast replace the device when it is damage.

#### BACKUP CONFIGURATION FILE

##### Backup to Localhost

  - File Name

Specify the File Name for the Startup-config file, which will be saved to the localhost.

##### Backup to USB

Ensure there is a USB stick inserted into the USB port.

  - Backup Running-config File

Specify the File Name for the saved Running-config file, which will be saved to the USB.

  - Backup Startup-config File

Specify the File Name for the saved Startup-config file, which will be saved to the USB.

Note: The file system of USB must be FAT32.

The “space” is not allowed in the File Name.

	   (Save Button)

Click the "Save" button to save the configuration file to the Localhost or USB.

NOTE: If the File Name filed is empty, the system assigns the default name: config-[datetime].cfg

# Config Restore

We suggest users to save/backup the configurations after a series of settings. If another device needs the same configurations, users can use the Config Restore function to restore it.

#### RESTORE CONFIGURATION FILE

##### Restore from Localhost

  - File Name

Select the configuration file, which is saved in the Localhost.

##### Restore from USB

Please ensure there is a USB stick inserted into the USB port.

  - File Name in USB

The File Name of the saved configuration file, which is saved to the USB. If the configuration file is saved in the directory, please specify the full path.

Note: The file system of USB must be FAT32.

The “space” is not allowed in the File Name.

	  (Restore Button)

Click the "Restore" button to restore the configurations from the Localhost or USB.

# USB Auto-Load & Auto-Backup

CONFIGURE USB AUTO-LOAD AND AUTO-BACKUP

##### USB Auto-Load

“Enable” or “Disable” the USB Auto-Load function. If “USB Auto-Load” is enabled, the system will search the configuration file named “startup-config” in the USB and load it when rebooting.

Note: The file system of USB must be FAT32.

##### USB Auto-Backup

“Enable” or “Disable” USB Auto-Backup function. If “USB-Auto-Backup” is enabled, the system will save the configurations to a file named “running-config” in the USB when users modify the configurations.

Note: The file system of USB must be FAT32.

	   (Apply Button)

After configuring above fields, click "Apply" button to make the changes effective.

# SFTP File Access

CONFIGURE SFTP CONFIGURATION UPLOAD

- Config IP address of SFTP server

Switch(config)# upload server ip [SERVER_IP]

- Config login account name of SFTP server

Switch(config)# upload sftp server account [SERVER_ACCOUNT]

- Config login account password of SFTP server

Switch(config)# upload sftp server password [SERVER_PASSWORD]

- Action to do the SFTP upload

Switch(config)# upload sftp

CONFIGURE SFTP CONFIGURATION DOWNLOAD

- Config IP address of SFTP server

Switch(config)# copy sftp ip [SERVER_IP]

- Config login account name for SFTP server

Switch(config)# copy sftp account [SERVER_ACCOUNT]

- Config login account password for SFTP server

Switch(config)# copy sftp password [SERVER_PASSWORD]

- Config login account password for SFTP server

Switch(config)# copy sftp file name [FILE_NAME]

- Action to do the SFTP download to the startup configuration

Switch(config)# copy sftp startup-config

Note: After copy to the startup configuration, system will reboot automatically.

- Action to do the SFTP download to the USB storage

Switch(config)# copy sftp USB

Note: The file system of USB must be FAT32.

# Command Line Interface

Command Line Interface is usually called CLI. It allows the users to configure, monitor, and maintain the switch by executing commands directly.

CONNECT TO CLI VIA CONSOLE PORT

Before starting the connection to the Console Port, ensure that you have a utility (such as “Putty”, “Tera Term”, “HyperTerminal”, “SecureCRT”, etc.) to do that. The following example is operating on Windows 7 and connected by “Putty”.

- Connect the Console Port to your PC or Laptop and check the port number in the “Device Manager” on the PC.

- Configure the Serial Information with the COM port number and Speed (Baud Rate: 115200). By default, the Data bits and Parity are 8 and 1. Then click “Open” to connect to the CLI.

Note: The complete parameters are COMX/115200/8/1.

- Enter the username and password to login to the system. The default username and password is admin/admin.

- When you see “Switch>”, it refers that you have logged in to the system. You can then start to configure the system on the CLI mode.

CONNECT TO CLI VIA TELNET

The following example is operating on Windows 7. If the system shows the information as the picture below, please enable the “Telnet Client” before using telnet function.

- Click Windows “Start” button and enter “cmd” on the search box to open the “Command Prompt”.

- Enter “telnet [IP_ADDRESS]” on the CMD window. For example, the IP address of the switch is “192.168.10.166”, so enter “telnet 192.168.10.166” and then press the “Enter” key.

- Enter the username and password to login the system. The default username and password is

admin/admin.

- When “Switch>” is displayed, it refers that you have logged in to the system. You can then start to configure the system on the CLI mode.

CONFIGURE SYSTEM UNDER DIFFERENT MODES

After login to CLI, users must enter the Privileged Mode for “show” commands. If users want to configure the system via CLI, they must enter Configuration Mode.

The command to enter Privileged Mode is “enable”. After entering Privileged Mode, issue “configure terminal” to enter Configuration Mode. When “Switch(config)#” is displayed, users can start configuring the system with all commands under Configuration Mode. In the Command Group section, the mode of each command will be marked in the last column of the commands table.

There are different modes under Configuration Mode, such as Interface Mode, VLAN Mode, ERPS Mode, and MRP Mode. If the command that users are preparing to issue is under these modes, they must enter the designated mode first. Users can issue “exit” to leave current mode. In the following table, we list the commands to enter different modes.

| Mode | Command | Description |
| --- | --- | --- |
| Interface | interface lanX | X implies the port number |
| VLAN | vlan X | X implies the VLAN ID |
| ERPS | ethernet redundancy erps-ring X | X implies the Ring number, from 1 to 3 |
| MRP | ethernet redundancy mrp instance-mode 1 | Only support single ring currently |

#### ENABLE TELNET CLIENT ON WIDOWS 7

- Click the Windows “Start” button and click “Control Panel” item.

- Click the “Programs” item.

- Click the “Turn Windows features on or off” item.

- Select the checkbox of “Telnet Client” and then click “OK” to enable telnet function.

- Click Windows “Start” button and enter “cmd” on the search box to open the “Command Prompt” to test the telnet function.

FIRMWARE UPGRADE VIA CLI

Users can upgrade the system with a new firmware on both the web console and CLI mode. To upgrade on the web console, a high interactivity web GUI is provided for the users. Please refer to

Firmware Upgrade section. To upgrade on the CLI mode, there are 3 methods: TFTP, wget (HTTP), and USB. The following sections explain how to upgrade the firmware using the 3 methods.

FIRMWARE UPGRADE VIA CLI – TFTP

If the users are planning to upgrade the firmware via CLI mode with TFTP, a TFTP server is needed before upgrading. You can download the free TFTP server from tftpd official website.

- Open the TFTP Server and browser the file directory path. For example, if the firmware file is saved on the desktop, the path to the desktop should be specified in the “Current Directory” field.

- Make sure the link between the switch and the host (PC or laptop) is connected. To verify it, ping the IP address of the switch IP address from the host to check it.

- Assign the firmware file name by issuing the “upload file name [FILE_NAME]“. The default file name is “WEBFULL”.

- Assign the TFTP Server IP address by issuing “upload server ip [SERVER_IP]”. The server IP address is the IP address of the host, which is running the TFTP server.

The commands for assigning the filename and server IP are in the Configure mode, so before configuring, specify “configure terminal” to enter the Configure mode.

If the command is completely configured, the system will display “OK”.

- Start to upgrade the firmware file by specifying “upload tftp”. The system starts to upload the assigned file by the TFTP. This takes a few minutes.

- After uploading, the system will verify the uploaded file. If the verification passes, the new firmware file will be installed. Ensure the system is powered on and the system will reboot automatically after the firmware is completely installed.

FIRMWARE UPGRADE VIA CLI – WGET

“Wget” uses the HTTP to transmit the file to the switch. Users must establish a HTTP Server

such as “Apache” and upload the firmware file to the HTTP Server.

- Assume there is a HTTP Server existed whose IP address is “192.168.1.9” and the firmware file named WEBFULL-v1.0.0 is uploaded.

- Make sure the link between the switch and the server is connected. We can ping the IP address of the server from the switch by using the command “ip ping [IP_ADDRESS]”.

- Assign the firmware file name by using “upload file name WEBFULL-v1.0.0“.

- Assign the Wget Server IP address by using “upload server ip 192.168.1.9”. If the command is completely configured, the system will display “OK”.

- Start to upgrade the firmware file by using “upload wget”. The system starts to upload the assigned file by HTTP. This takes a few seconds or minutes.

- Once the uploading is complete, the system will verify the uploaded file. If the verification passes, the new firmware file will be installed. Ensure to keep the system powered on and the system will reboot automatically after the firmware is completely installed.

FIRMWARE UPGRADE VIA CLI – USB

Check if the firmware file is saved in the USB and the USB stick is inserted in the USB part of the switch before upgrading the firmware file.

- Save the firmware file to the USB device and insert the USB stick to the USB port.

- Use “copy usb firmware [FILE_NAME]” to upgrade the system via USB.

- After the installation is complete, the system will reboot automatically.

Note: The file system of USB must be FAT32.

#### COMMAND GROUPS

The following are the commands that the users can use in the CLI mode. Please check if the

mode is correct before issuing the command.

#### AUTHENTICATION GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| login authentication [tacacs+ ¦ radius] | Set login authentication method | Configure |
| logout | Disconnect | Configure |
| radius-server host [IP_ADDR] | Set IP address of RADIUS server | Configure |
| radius-server key [SHARED_KEY] | Set specific characters for authentication verification | Configure |
| radius-server port [1-65535] | Set communication port of RADIUS server | Configure |
| radius-server retransmit [1-1000] | Set the number of times a request re-sending to RADIUS server | Configure |
| radius-server timeout [1-1000] | Set the timeout period to wait for RADIUS server response | Configure |
| tacacs-server host [IP_ADDR] | Set IP address of TACASC+ server | Configure |
| tacacs-server key [SHARED_KEY] | Set specific characters for authentication verification | Configure |
| tacacs-server port [1-65535] | Set communication port of TACASC+ server | Configure |
| tacacs-server timeout [1-1000] | Set the timeout period to wait for TACASC+ server response | Configure |
| username [USER_ID] [PASSWORD] | Configure username and password | Configure |
| username-ro [USER_ID] [PASSWORD] | Configure read only username and password | Configure |
| show login authentication | Display login authentication method | Configure |
| show radius-server host | Display IP address of RADIUS server | Configure |
| show radius-server key | Display specific characters for authentication verification | Configure |
| show radius-server port | Display communication port of RADIUS server | Configure |
| show radius-server retransmit | Display the number of times a request is resent | Configure |
| show radius-server timeout | Display the timeout period to wait for RADIUS server response | Configure |
| show tacacs-server host | Display IP address of the server | Configure |
| show tacacs-server key | Display specific characters for authentication verification | Configure |
| show tacacs-server port | Display communication port of the server | Configure |
| show tacacs-server timeout | Display the timeout period to wait for the server response | Configure |
| show username | Display admin ID | Configure |
| show username-ro | Display read only user ID | Configure |
| no login authentication | Default Login authentication method | Configure |
| no radius-server host | Default IP address of the server | Configure |

| no radius-server key | Default specific characters for authentication verification | Configure |
| --- | --- | --- |
| no radius-server port | Default communication port of the server | Configure |
| no radius-server retransmit | Default the number of times a request is resent | Configure |
| no radius-server timeout | Default the timeout period to wait for the server response | Configure |
| no tacacs-server host | Default IP address of TACACS+ server | Configure |
| no tacacs-server key | Default specific characters for authentication verification | Configure |
| no tacacs-server port | Default communication port of TACACS+ server | Configure |
| no tacacs-server timeout | Default the timeout period to wait for TACACS+ server response | Configure |
| no username | Default username and password | Configure |
| no username-ro | Default read only username and password | Configure |

SSH GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| copy host-key-config usb [FILE_NAME] | Backup SSH host key to USB | Configure |
| copy usb host-key-config [file] | Upload SSH host key config from USB | Configure |
| download file name [FILE_NAME] | Set downloading file name, default name is host_key.cfg | Configure |
| download host-key-config | Download current SSH host key config | Configure |
| download server account [SERVER_ACCOUNT] | Set downloading server account | Configure |
| download server ip [SERVER_IP] | Set downloading server IP Address | Configure |
| download server password [SERVER_PASSWORD] | Set downloading server password | Configure |
| upload host-key-config wget [file] | Upload SSH host key config from Localhost | Configure |
| show ssh host-key | Display SSH host key | Configure |

#### SYSTEM GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| erase startup-config | Reset to factory default and reboot | Configure |
| erase startup-config keep-ip | Reset to factory default except IP | Configure |
| erase startup-config keep-ip-user | Reset to factory default except IP and USER | Configure |
| erase startup-config keep-user | Reset to factory default except USER ID/PASS | Configure |
| exec-timeout [MINUTE] [SECOND] | Set idle timeout [MINUTE] [SECOND] | Configure |
| hostname [HOSTNAME] | Set Switch Host Name | Configure |
| reboot | Reboot the switch | Configure |
| system contact [CONTACT] | Set system contact | Configure |
| system description [SYS_DESCRIPTION] | Set device description | Configure |
| system location [LOCATION] | Set device location | Configure |

| show exec-timeout | Display idle timeout | Configure |
| --- | --- | --- |
| show hostname | Display Switch Host Name | Configure |
| show environment power [1¦2] | Display power 1/2 status | Configure |
| show event status relay | Display relay status | Configure |
| show system contact | Display system contact | Configure |
| show system description | Display system description | Configure |
| show system firmware-date | Display system release time | Configure |
| show system location | Display system location | Configure |
| show system mac | Display system MAC address | Configure |
| show system uptime | Display system uptime | Configure |
| show system version firmware | Display system version | Configure |
| show transceiver ddm | Display transceiver DDM information | Interface |
| show transceiver info | Display transceiver information | Interface |
| show transceiver raw | Display transceiver raw data | Interface |
| show username | Display admin ID | Configure |
| no exec-timeout | Default idle timeout | Configure |
| no hostname | Default Switch Host Name | Configure |
| no system contact | Clear system contact | Configure |
| no system description | Clear device description | Configure |
| no system location | Clear device location | Configure |
| no username | Default username and password | Configure |

SERVICE CONTROL GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| service [http ¦ https ¦ ssh ¦ telnet ¦ console ¦ reset-button] enable | Enable service http, https, ssh, telnet, console port, or reset button | Configure |
| show service [http ¦ https ¦ ssh ¦ telnet ¦ console ¦ reset-button] | Display service http, https, ssh, telnet, console port, or reset button state | Configure |
| no service [http ¦ https ¦ ssh ¦ telnet ¦ console ¦ reset-button] | Disable service http, https, ssh, telnet, console port, or reset button | Configure |

IPV4 GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ip address [IP_ADDR] [MASK] | Set IPv4 address and netmask | VLAN |
| ip loopback-address [IP_ADDR] [NETMASK] | Set Loopback Address | Configure |
| ip name-server [NAME_SERVER_IP] | Set Domain Name-Server | Configure |
| ip ping [IPV4_ADDR] [<size PKG_SIZ> ¦ <repeat PKG_CNT>] | Issue an IPv4 ping command | Configure |
| show ip address | Display Host address of IPv4 | VLAN |
| show ip loopback-address | Display Loopback address of IPv4 | Configure |
| show ip name-server | Display Domain Name-Server | Configure |

| no ip address | Delete IPv4 address | VLAN |
| --- | --- | --- |
| no ip loopback-address | Delete Loopback Address | Configure |
| no ip name-server | Clear the domain name-server | Configure |

IPV6 GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ipv6 address [X:X::X:X</PREFIX_LEN>] | Set VLAN IPv6 Address | VLAN |
| ipv6 enable | Enable IPv6 protocol | Configure |
| ipv6 ping [IPV6_ADDR] [<size PKG_SIZ> ¦ <repeat PKG_CNT>] | Issue an IPv6 ping command | Configure |
| show ipv6 | Display IPv6 protocol state | Configure |
| show vlan ipv6 | Display VLAN IPv4 Address Table | Configure |
| no ipv6 | Disable IPv6 protocol | Configure |
| no ipv6 address [IPV6_ADDR/PREFIX_LEN] | Delete IPv6 address | VLAN |

#### TIME GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| clock time [hh:mm:ss] [day] [month] [year] | Configure time | Configure |
| clock timezone [AREA] [CITY] | Configure time zone | Configure |
| ntp client sync [minute ¦ hour ¦ day ¦ month ¦ year] [NUMBER] | Configure NTP client sync | Configure |
| ntp client timeserver1 [SERVER_IP/URL] | Configure NTP client time server 1 | Configure |
| ntp client timeserver2 [SERVER_IP/URL] | Configure NTP client time server 2 | Configure |
| ntp time update | Configure NTP time update | Configure |
| show clock time | Show time | Configure |
| show clock timezone | Show timezone | Configure |
| show ntp client sync | Show sync time | Configure |
| show ntp client timeserver1 | Show NTP server 1 configuration | Configure |
| show ntp client timeserver2 | Show NTP server 2 configuration | Configure |
| no clock timezone | Remove timezone | Configure |
| no ntp client sync | Remove NTP sync time | Configure |
| no ntp client timeserver1 | Remove NTP time server 1 configuration | Configure |
| no ntp client timeserver2 | Remove NTP time server 2 configuration | Configure |

PTP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ptp announce interval [-1 to 7] | Set PTP announce interval, the interval is expressed as log 2. i.e. -1 is 0.5s, 0 is 1s. | Configure |
| ptp announce timeout [2-255] | Set PTP announce timeout | Configure |
| ptp disable | Disable PTP | Configure |

| ptp domain [0-127] | Set PTP domain number | Configure |
| --- | --- | --- |
| ptp enable | Enable PTP | Configure |
| ptp interface1 | Set the interface to master of boundary clock mode | Configure |
| ptp interface2 | Set the interface to slave of boundary clock mode | Configure |
| ptp mode [m(master) ¦ s(slave) ¦ b(boundary clock)] | Set PTP mode |  |
| ptp period [0-20] | Set PTP timeout periods | Configure |
| ptp priority1 [0-248] | Set PTP priority1 | Configure |
| ptp priority2 [0-248] | Set PTP priority2 | Configure |
| ptp sync interval [-7 to 7] | Set PTP sync interval, the interval is expressed as log 2. i.e. -1 is 0.5s, 0 is 1s. | Configure |
| show ptp announce interval | Display PTP announce interval | Configure |
| show ptp announce timeout | Display PTP announce timeout | Configure |
| show ptp clock | Display PTP sync information | Configure |
| show ptp domain | Display PTP domain number | Configure |
| show ptp enable | Display PTP status | Configure |
| show ptp interface1 | Display PTP interface1 | Configure |
| show ptp interface2 | Display PTP interface2 | Configure |
| show ptp mode | Display PTP mode | Configure |
| show ptp period | Display PTP timeout periods | Configure |
| show ptp priority1 | Display PTP priority1 | Configure |
| show ptp priority2 | Display PTP priority2 | Configure |
| show ptp sync interval | Display PTP sync interval | Configure |
| no ptp announce interval | Default PTP announce interval | Configure |
| no ptp announce timeout | Default PTP announce timeout | Configure |
| no ptp domain | Default PTP domain number | Configure |
| no ptp interface1 | Default PTP interface1 | Configure |
| no ptp interface2 | Default PTP interface2 | Configure |
| no ptp mode | Default PTP mode | Configure |
| no ptp period | Default PTP timeout periods | Configure |
| no ptp priority1 | Default PTP priority1 | Configure |
| no ptp priority2 | Default PTP priority2 | Configure |
| no ptp sync interval | Default PTP sync interval | Configure |

STP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| spanning-tree forward-time [4-30] | Set STP forward time | Configure |
| spanning-tree hello-time [1-10] | Set STP hello time | Configure |
| spanning-tree max-age [6-40] | Set max age | Configure |

| spanning-tree mode [rstp] | Set STP mode as [RSTP] | Configure |
| --- | --- | --- |
| spanning-tree mst instance [1-15] vlan [VLAN_LIST] | Set vlan group for specific MSTP instance | Configure |
| spanning-tree mst name [NAME] | Set MSTP name | Configure |
| spanning-tree mst revision [0-65535] | Set MSTP revision | Configure |
| spanning-tree mst [1-15] priority [0-61440] | Set priority for specific MSTP instance | Configure |
| spanning-tree priority [0-61440] | Set STP priority | Configure |
| spanning-tree cost [0-200000000] | Configure STP cost | Interface |
| spanning-tree edge [admin-edge¦admin-non-edge] | Configure STP edge | Interface |
| spanning-tree link-type [point-to-multiple¦point-to-point] | Configure STP link type on port | Interface |
| spanning-tree mst [1-15] cost [0- 200000000] | Configure port cost for specific MSTP instance | Interface |
| spanning-tree mst [1-15] port-priority [0- 200000000] | Configure port priority for specific MSTP instance | Interface |
| spanning-tree port-priority [0-240] | Configure STP port priority | Interface |
| spanning-tree stp disable | Disable Spanning Tree Protocol (STP) on port | Interface |
| show spanning-tree forward-time | Show STP forward time | Configure |
| show spanning-tree hello-time | Show STP hello time | Configure |
| show spanning-tree max-age | Show STP max age | Configure |
| show spanning-tree mode | Show Spanning Tree mode (RSTP or disable) | Configure |
| show spanning-tree mst instance [1-15] vlan | Show vlan group for specific MSTP instance | Configure |
| show spanning-tree mst name | Show MSTP name | Configure |
| show spanning-tree mst revision | Show MSTP revision | Configure |
| show spanning-tree mst [1-15] priority | Show priority for specific MSTP instance | Configure |
| show spanning-tree mst [1-15] status | Show bridge status for specific MSTP instance | Configure |
| show spanning-tree priority | Show STP priority | Configure |
| show spanning-tree rstp-status | Show Spanning Tree rstp status | Configure |
| show spanning-tree cost | Show STP cost | Interface |
| show spanning-tree edge | Show STP auto edge | Interface |
| show spanning-tree link-type | Show STP link type | Interface |
| show spanning-tree mst [1-15] cost | Show port cost for specific MSTP instance | Interface |
| show spanning-tree mst [1-15] port-priority | Show port priority for specific MSTP instance | Interface |
| show spanning-tree port-priority | Show STP port priority | Interface |
| show spanning-tree stp | Show STP activated status on port | Interface |
| no spanning-tree forward-time | Remove STP forward time configuration | Configure |
| no spanning-tree hello-time | Remove STP hello time configuration | Configure |
| no spanning-tree max-age | Remove STP max age configuration | Configure |
| no spanning-tree mode | Disable STP configuration | Configure |
| no spanning-tree priority | Remove STP priority configuration | Configure |

| no spanning-tree cost | Remove STP cost configuration | Interface |
| --- | --- | --- |
| no spanning-tree edge | Remove auto edge configuration | Interface |
| no spanning-tree link-type | Remove link type configuration | Interface |
| no spanning-tree mst [1-15] cost | Remove port cost for specific MSTP instance | Interface |
| no spanning-tree mst [1-15] port-priority | Remove port priority for specific MSTP instance | Interface |
| no spanning-tree port-priority | Remove STP port priority configuration | Interface |
| no spanning-tree stp | Enable STP on port | Interface |

ERPS GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ethernet redundancy erps-ring [ 1 ¦ 2 ¦ 3 ] | Ethernet Ring Protection Switching (ERPS) mode | Configure |
| aps-channel [1 - 4094] | Set APS channel | ERPS |
| disable | Disable ERPS function | ERPS |
| enable | Enable ERPS function | ERPS |
| erps-ring [ 1 ¦ 2 ¦ 3 ] | Change to Other ERPS Ring | ERPS |
| ext-command clear | Extended ERPS command - Clear | ERPS |
| ext-command fs | Extended ERPS command – Forced Switch | ERPS |
| ext-command ms | Extended ERPS command – Manual Switch | ERPS |
| id [1 - 239] | Set Ring ID | ERPS |
| mel [0 - 7] | ERPS mel | ERPS |
| revertive | Set as revertive mode | ERPS |
| ring-port 0 [1(lan1) - N(lanN)] | Mapping ERPS ring port0 to switch port | ERPS |
| ring-port 1 [1(lan1) - N(lanN)] | Mapping ERPS ring port1 to switch port | ERPS |
| role port0 [o(owner) ¦ n(neigh) ¦ i(interconn)] | Set role on ring port0 | ERPS |
| role port1 [o(owner) ¦ n(neigh) ¦ i(interconn)] | Set role on ring port1 | ERPS |
| timer guard [10 - 2000] | Set guard timer interval | ERPS |
| timer hold-off [0 - 10000] | Set hold-off timer interval | ERPS |
| timer wtr [1 - 12] | Set WTR timer interval | ERPS |
| type [m(major-ring) ¦ s(sub-ring)] | Set type as Major-Ring or Sub-Ring | ERPS |
| virtual-channel major-ring channel-id [1-4094] | Set virtual channel for ERPS Ring | ERPS |
| virtual-channel sub-ring set | Set virtual channel for ERPS Sub-ring | ERPS |
| show config | Displays ERPS configuration | ERPS |
| show port status | Displays ERPS ring port status | ERPS |
| show status | Displays ERPS status | ERPS |
| no aps-channel | Default ERPS aps-channel | ERPS |
| no id | Default Ring ID as default | ERPS |
| no revertive | Default mode non-revertive | ERPS |
| no ring-port 0 | Default ring port0 as lan1 | ERPS |
| no ring-port 1 | Default ring port1 as lan2 | ERPS |

| no role port0 | Default role of ring port0 as none | ERPS |
| --- | --- | --- |
| no role port1 | Default role of ring port1 as none | ERPS |
| no timer guard | Default guard timer | ERPS |
| no timer hold-off | Default hold-off timer | ERPS |
| no timer wtr | Default wtr timer | ERPS |
| no type | Default ring type as Major-Ring | ERPS |
| no virtual-channel major-ring channel-id | Default virtual channel as ERPS Major Ring's aps-channel | ERPS |
| no virtual-channel sub-ring set | Default virtual channel for ERPS Sub-ring as None | ERPS |

MRP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ethernet redundancy mrp instance-mode [1] | Media Redundancy Protocol (MRP) mode | Configure |
| advanced-mode [enable ¦ disable] | Enable/Disable MRP Advanced Mode | MRP |
| domain-id [DOMAIN_ID] | Set MRP Domain-id, the format is 16 bytes in decimal notation | MRP |
| name [DOMAIN_NAME] | Set MRP Domain Name | MRP |
| operation [enable ¦ disable] | Enable/Disable MRP Protocol | MRP |
| port 1 [1(lan1) - N(lanN)] | Set MRP ring-port 1 ID | MRP |
| port 2 [1(lan1) - N(lanN)] | Set MRP ring-port 2 ID | MRP |
| recovery-delay [500 ¦ 200] | Set MRP Recovery Delay (unit: ms) | MRP |
| role [m(manager) ¦ c(client)] | Set MRP Role to MRM(manager) or MRC(client) | MRP |
| show advanced-mode | Display MRP Advanced-mode | MRP |
| show config | Display MRP Domain Config | MRP |
| show domain-id | Display MRP Domain ID | MRP |
| show name | Display MRP Domain Name | MRP |
| show operation | Display MRP Operation Status | MRP |
| show port [1 ¦ 2] | Display MRP ring-port [1 ¦ 2] ID | MRP |
| show recovery-delay | Display MRP Recovery Delay | MRP |
| show role | Display MRP Domain Expected Role | MRP |
| show summary | Display MRP Domain Summary | MRP |
| no domain-id | Default MRP Domain ID | MRP |
| no name | Clear MRP Domain Name | MRP |
| no port [1 ¦ 2] | Default MRP ring-port [1 ¦ 2] ID | MRP |
| no recovery-delay | Default MRP Recovery Delay | MRP |
| no role | Default MRP Domain role | MRP |

SNMP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |

| snmp server community ro [COMMUNITY] | Set v1, v2c snmp server read-only community | Configure |
| --- | --- | --- |
| snmp server community rw [COMMUNITY] | Set v1, v2c snmp server read-write community | Configure |
| snmp server enable | Enable snmp server | Configure |
| snmp server enable v1-v2c-only | Enable snmp v1 and v2c | Configure |
| snmp server enable v3-only | Enable snmp v3 command only | Configure |
| snmp server v3 auth admin [md5¦ sha] [PASSWORD] | Set SNMPv3 admin authentication type | Configure |
| snmp server v3 auth user [md5¦ sha] [PASSWORD] | Set SNMPv3 user authentication type | Configure |
| snmp server v3 encryption admin [des¦ aes] [PASSWORD] | Set SNMPv3 admin encryption type | Configure |
| snmp server v3 encryption user [des¦ aes] [PASSWORD] | Set SNMPv3 user encryption type | Configure |
| snmp server v3 level admin [auth¦ noauth¦ priv] | Set SNMPv3 admin security level | Configure |
| snmp server v3 level user [auth¦ noauth¦ priv] | Set SNMPv3 user security level | Configure |
| snmp trap community [COMMUNITY] | Set v1, v2c snmp trap community | Configure |
| snmp trap host1 [TRAP_HOST_IP] | Set snmp trap host 1 IP address | Configure |
| snmp trap host2 [TRAP_HOST_IP] | Set snmp trap host 2 IP address | Configure |
| snmp trap inform retry [1-100] | Set snmp inform retry times | Configure |
| snmp trap inform timeout [1-300] | Set snmp inform timeout | Configure |
| snmp trap v3 auth [sha¦ md5] [PASSWORD] | Set SNMPv3 authentication type: md5 or sha | Configure |
| snmp trap v3 encryption [des¦ aes] [PASSWORD] | Set SNMPv3 encryption type: des or aes | Configure |
| snmp trap v3 engine-ID [ENGINE_ID] | Set snmp trap engine ID | Configure |
| snmp trap v3 level [auth¦ noauth¦ priv] | Set SNMPv3 trap security level | Configure |
| snmp trap v3 user [USER_ID] | Set SNMPv3 trap user | Configure |
| snmp trap version [1¦ 2c trap¦ 2c inform¦ 3 trap¦ 3 inform] | Set snmp trap version and type | Configure |
| show snmp server | Display snmp server status | Configure |
| show snmp server community ro | Display snmp server read only community | Configure |
| show snmp server community rw | Display snmp server writable community | Configure |
| show snmp server v3 auth admin | Display SNMPv3 admin authentication type and passphrase | Configure |
| show snmp server v3 auth user | Display SNMPv3 user authentication type and passphrase | Configure |
| show snmp server v3 encryption admin | Display SNMPv3 admin encryption type and passphrase | Configure |
| show snmp server v3 encryption user | Display SNMPv3 user encryption type and passphrase | Configure |
| show snmp server v3 level admin | Display SNMPv3 admin security level | Configure |

| show snmp server v3 level user | Display SNMPv3 user security level | Configure |
| --- | --- | --- |
| show snmp trap community | Display snmp trap community | Configure |
| show snmp trap host1 | Display snmp trap host 1 | Configure |
| show snmp trap host2 | Display snmp trap host 2 | Configure |
| show snmp trap inform retry | Display snmp inform retry times | Configure |
| show snmp trap inform timeout | Display snmp inform timeout | Configure |
| show snmp trap v3 auth | Display SNMPv3 authentication type and passphrase | Configure |
| show snmp trap v3 encryption | Display SNMPv3 encryption type and passphrase | Configure |
| show snmp trap v3 engine-ID | Display snmp trap engine ID | Configure |
| show snmp trap v3 level | Display SNMPv3 trap security level | Configure |
| show snmp trap v3 user | Display SNMPv3 trap user | Configure |
| show snmp trap version | Display snmp trap version and type | Configure |
| no snmp server | Disable snmp server | Configure |
| no snmp server community ro | Default ro-community name | Configure |
| no snmp server community rw | Default rw-community name | Configure |
| no snmp server v3 auth admin | Default SNMPv3 admin authentication type | Configure |
| no snmp server v3 auth user | Default SNMPv3 user authentication type | Configure |
| no snmp server v3 encryption admin | Default SNMPv3 admin encryption type | Configure |
| no snmp server v3 encryption user | Default SNMPv3 user encryption type | Configure |
| no snmp server v3 level admin | Default SNMPv3 admin security level | Configure |
| no snmp server v3 level user | Default SNMPv3 user security level | Configure |
| no snmp trap community | Default snmp trap community | Configure |
| no snmp trap host1 | Default snmp trap host 1 | Configure |
| no snmp trap host2 | Default snmp trap host 2 | Configure |
| no snmp trap inform retry | Default snmp inform retry times | Configure |
| no snmp trap inform timeout | Default snmp inform timeout | Configure |
| no snmp trap v3 auth | Default SNMPv3 authentication type and passphrase | Configure |
| no snmp trap v3 encryption | Default SNMPv3 encryption type and passphrase | Configure |
| no snmp trap v3 engine-ID | Default snmp trap engine ID | Configure |
| no snmp trap v3 level | Default SNMPv3 trap security level | Configure |
| no snmp trap v3 user | Default SNMPv3 trap user | Configure |
| no snmp trap version | Default snmp trap version | Configure |

DHCP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| boot host dhcp | Directs the system to get an IP address | Configure |

| dhcp relay information option | Set DHCP-relay option | Configure |
| --- | --- | --- |
| dhcp relay server [server_number: 1-4] [server_IP] | Set DHCP-relay server [1-4] IP | Configure |
| dhcp relay untrust | Set DHCP-relay untrusted port | Interface |
| dhcp server binding [bind_ID: 1 - 32] [MAC] [IP_TO_BIND] | Set binding IP and MAC of DHCP | Configure |
| dhcp server default-gateway [IP_ADDR] | Set default-gateway IP for DHCP client | Configure |
| dhcp server included-address [START_OF_IP] [END_OF_IP] | Set IP range for its client | Configure |
| dhcp server lease-time [60-2592000] | Set DHCP server lease time | Configure |
| dhcp server name-server [IP_ADDR] | Set name-server address for DHCP client | Configure |
| dhcp service relay enable | Enable DHCP relay | Configure |
| dhcp service server enable | Enable DHCP server | Configure |
| show boot host dhcp | Display DHCP client state | Configure |
| show dhcp relay information option | Display DHCP relay option | Configure |
| show dhcp relay server [server_number: 1-4] | Display DHCP relay address | Configure |
| show dhcp relay untrust | Display DHCP untrusted port status | Interface |
| show dhcp server binding | Display all DHCP bounding entries | Configure |
| show dhcp server default-gateway | Display DHCP default-gateway IP | Configure |
| show dhcp server included-address | Display DHCP included IP range | Configure |
| show dhcp server lease | Display DHCP lease entries | Configure |
| show dhcp server lease-time | Display DHCP server lease time | Configure |
| show dhcp server name-server | Display DHCP name-server | Configure |
| show dhcp server status | Display DHCP server status | Configure |
| show dhcp service relay | Display DHCP relay agent status | Configure |
| show dhcp service server | Display DHCP server status | Configure |
| no boot host dhcp | Disable DHCP client | Configure |
| no dhcp relay information option | Disable DHCP relay option | Configure |
| no dhcp relay server [server_number: 1-4] | Remove DHCP relay server [1-4] IP | Configure |
| no dhcp relay untrust | Default port as trusted | Interface |
| no dhcp server binding [bind_ID: 1-32] | Remove DHCP bounding IP and MAC | Configure |
| no dhcp server default-gateway | Remove DHCP default-gateway IP | Configure |
| no dhcp server included-address | Remove DHCP included IP range | Configure |
| no dhcp server lease-time | Remove DHCP lease time | Configure |
| no dhcp server name-server | Remove DHCP name-server | Configure |
| no dhcp service relay | Disable DHCP relay | Configure |
| no dhcp service server | Disable DHCP server | Configure |

#### INDUSTRIAL PROTOCOLS GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ethernet-ip enable | Enable EtherNet/IP Protocol | Configure |
| modbus tcp enable | Enable Modbus/TCP Protocol | Configure |
| profinet enable | Enable PROFINET Protocol | Configure |
| show ethernet-ip | Show EtherNet/IP status | Configure |
| show modbus tcp | Show Modbus/TCP status | Configure |
| show profinet | Show PROFINET status | Configure |
| no ethernet-ip | Disable EtherNet/IP Protocol | Configure |
| no modbus tcp | Disable Modbus/TCP Protocol | Configure |
| no profinet | Disable PROFINET Protocol | Configure |

UPNP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| upnp advertisement interval [300-86400] | Set UPnP advertisement interval | Configure |
| upnp enable | Enable Universal Plug and Play (UPnP) | Configure |
| show upnp | Display Universal Plug and Play (UPnP) state | Configure |
| show upnp advertisement interval | Display UPnP advertisement interval | Configure |
| no upnp | Disable Universal Plug and Play (UPnP) | Configure |
| no upnp advertisement interval | Default UPnP advertisement interval | Configure |

#### PORT GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| eee port-enable | 802.3az (EEE) port enable | Interface |
| flowcontrol [on ¦ off] | Configure port's flow-control to response a pause frame | Interface |
| name [PORT_NAME] | Set interface name | Interface |
| shutdown | Disable port | Interface |
| speed_duplex [10 ¦ 100] [full ¦ half] | Configure port's speed and duplex | Interface |
| show interface all link summary | To display interface link status globally | Configure |
| show administrate | To display port's admin state | Interface |
| show eee port-all | Display EEE port-all status | Configure |
| show eee-info | Display Port EEE statistic information | Interface |
| show flowcontrol | Display port's flow-control state | Interface |
| show link duplex | To display port's duplex | Interface |
| show link rx | To display port's Rx_Bytes | Interface |
| show link speed | To display port's speed | Interface |
| show link state | To display port's link state | Interface |
| show link summary | To display port's link summary | Interface |

| show link tx | To display port's Tx_Bytes | Interface |
| --- | --- | --- |
| show name | To display port's name | Interface |
| show speed_duplex | To display port's speed and duplex | Interface |
| show transceiver | Transceiver information | Interface |
| no eee port-enable | 802.3az (EEE) port disable | Interface |
| no flowcontrol | Default flow-control as Auto mode | Interface |
| no name | Remove port's name | Interface |
| no shutdown | Enable port | Interface |
| no speed_duplex | Default port speed-duplex as Auto mode | Interface |

POE GROUP (PoE Model Only)

| Command | Explanation | Mode |
| --- | --- | --- |
| power inline budget [1-240] | Power PoE budget | Configure |
| power inline mode-config disable | Disable PoE on port | Interface |
| power inline mode-config enable | Enable PoE on port | Interface |
| power inline mode-config force | Force PoE powered on port | Interface |
| power inline priority [1-3] | Set PoE port priority on port; 1:high, 2:middle, 3:low | Interface |
| keepalive enable | Enable PoE keepalive | Interface |
| keepalive hold-time | Configure PoE keepalive power cycle hold-time | Interface |
| keepalive ip | Configure IP for PoE keepalive | Interface |
| keepalive time | Configure PoE keepalive cycle time | Interface |
| schedule enable | Enable one port PoE schedule | Interface |
| schedule [Sunday-Saturday] open-time [time] | Configure PoE schedule open time on one day | Interface |
| show power inline budget | Display PoE power budget | Configure |
| show power inline detail-code | Display PoE status code, refer to “PoE Debug Code” for more explanation | Interface |
| show power inline operation | Display All PoE ports operation status | Configure |
| show power inline status | Display All PoE ports detail status | Configure |
| show power inline status | Display PoE status for specific port | Interface |
| show power inline temperature | Display temperature of PoE controller | Configure |
| show keepalive table | Display All PoE keepalive info | Configure |
| show power inline status | Display PoE status | Interface |
| show keepalive | Show PoE keepalive status | Interface |
| show keepalive hold-time | Show PoE keepalive hold-time | Interface |
| show keepalive ip | Show IP for PoE keepalive | Interface |

| show keepalive time | Show PoE keepalive cycle time | Interface |
| --- | --- | --- |
| show schedule | Disable Universal Plug and Play (UPnP) | Interface |
| show schedule [Sunday-Saturday] open-time | Show open time of POE schedule on one day | Interface |
| show schedule table | Show one port PoE schedule table | Interface |
| no power inline budget | Default PoE power budget | Configure |
| no power inline mode-config | Default PoE powered config on port | Interface |
| no power inline priority | Disable PoE port priority on port | Interface |
| no keepalive | Disable PoE keepalive | Interface |
| no keepalive hold-time | Default PoE keepalive power cycle hold-time | Interface |
| no keepalive ip | Remove IP for PoE keepalive | Interface |
| no keepalive time | Remove PoE keepalive cycle time | Interface |
| no schedule | Remove one port PoE schedule | Interface |
| no schedule [Sunday-Saturday] open-time | Remove PoE schedule on one day | Interface |

IGMP SNOOPING GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| igmp snooping enable | Enable IGMP snooping | Configure |
| igmp snooping last-member count [2-10] | Set IGMP last-member-count | Configure |
| igmp snooping last-member interval [1-25] | Set IGMP last-member-interval | Configure |
| igmp snooping querier enable | Enable IGMP snooping querier | Configure |
| igmp snooping query interval [1-3600] | Set IGMP query interval | Configure |
| igmp snooping query max-respond-time [1-12] | Set IGMP max-query-respond time | Configure |
| igmp snooping query version [VLAN_ID] [STATE:0¦1] [VERSION:1¦2¦3] | Add IGMP query version entry by VLAN ID. STATE 0: disable; STATE 1: enable | Configure |
| igmp snooping router-port [PORT_LIST] | Set router port list for multicast | Configure |
| igmp snooping unknown-multicast [f¦d¦r] | Set unknown-multicast action | Configure |
| show igmp snooping all | Display IGMP settings (summary) | Configure |
| show igmp snooping mdb | Display IGMP multicast database | Configure |
| show igmp snooping query-version | Display IGMP Query version by VLAN ID | Configure |
| show igmp snooping router-port | Display IGMP router port list | Configure |
| show igmp snooping unknown-multicast | Display unknown-multicast action | Configure |
| no igmp snooping | Disable IGMP snooping | Configure |
| no igmp snooping last-member count | Default IGMP Last-Member-Count | Configure |
| no igmp snooping last-member interval | Default IGMP Last-Member-Interval | Configure |
| no igmp snooping querier | Disable IGMP querier | Configure |
| no igmp snooping query interval | Default IGMP query interval | Configure |
| no igmp snooping query max-respond-time | Default IGMP max-respond-time | Configure |

| no igmp snooping router-port | Default IGMP router port | Configure |
| --- | --- | --- |
| no igmp snooping unknown-multicast | Default unknown-multicast action | Configure |

VLAN GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| provider ethertype [VALUE_IN_HEX (i.e., 0x88A8)] | Setup EtherType in S-TAG for provider port | Configure |
| member [untag PORT_LIST] [tag PORT_LIST] | Set VLAN member | VLAN |
| name [VLAN_NAME] | Set VLAN Name | VLAN |
| switchport accept [tagged ¦ untagged] | Set VLAN acceptance of frame | Interface |
| switchport mode [d(dot1q-tunnel)¦ c(customer)¦ p(provider)¦ s(specific-provider)] | Configure port type as dot1q-tunnel, Customer, or Service Provider | Interface |
| switchport pvid [PVID: 1-4094] | Set port VLAN-Id | Interface |
| show provider ethertype | Display Service Provider EtherType | Configure |
| show vlan global | Display VLAN Global information | Configure |
| show member | Display port VLAN member | VLAN |
| show name | Display VLAN name | VLAN |
| show switchport accept | Display acceptance of VLAN frame | Interface |
| show switchport mode | Display VLAN interface port type | Interface |
| show switchport pvid | Display port VLAN-Id | Interface |
| no provider ethertype | Default EtherType as 0x88A8 in S-TAG for provider port | Configure |
| no member | Default VLAN member | VLAN |
| no name | Default VLAN name | VLAN |
| no switchport accept | Default acceptance of VLAN frame | Interface |
| no switchport mode | Default port type as Customer | Interface |
| no switchport pvid | Default port VLAN-Id | Interface |

QOS GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| qos fair-queue weight [W0] [W1] [W2] [W3] [W4] [W5] [W6] [W7] | Set WRR Queue Weight | Configure |
| qos map cos [priority:0-7] to tx-queue [0-7] | Set Cos queue mapping of priority [0-7] | Configure |
| qos map dscp [0-63] to tx-queue [0-7] | Set DSCP mapping queue | Configure |
| qos queue-schedule [strict ¦ wrr] | Set QoS scheduling type | Configure |
| qos default cos [0-7] | Set Default Class of Service (COS) value | Interface |

| qos trust [cos ¦ dscp] | Set trust of cos or dscp | Interface |
| --- | --- | --- |
| show qos fair-queue weight | Display WRR Queue Weight | Configure |
| show qos map cos | Display global QoS queue mapping status | Configure |
| show qos map cos [0-7] | Display QoS queue mapping status of Priority [0-7] | Configure |
| show qos map dscp | Display global DSCP queue mapping status | Configure |
| show qos map dscp [0-63] | Display DSCP queue mapping status of class [0-63] | Configure |
| show qos queue-schedule | Display queue scheduling type | Configure |
| show qos default cos | Display CoS default value | Interface |
| show qos trust | Display QoS trust | Interface |
| no qos fair-queue weight | Default WRR Queue Weight | Configure |
| no qos map cos [0-7] | Reset Cos queue mapping of priority [0-7] | Configure |
| no qos map dscp [0-63] | Reset DSCP mapping queue to default | Configure |
| no qos queue-schedule | Default scheduling type as WRR | Configure |
| no qos default cos | Reset default CoS to initial value | Interface |
| no qos trust | Default trust as CoS | Interface |

#### PORT TRUNK GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| trunk group [1-8] [static ¦ lacp] INTERFACES_LIST | Configure port aggregation group | Configure |
| show trunk group | Show all trunk groups | Configure |
| show trunk group [1-8] | Show trunk group [1-8] | Configure |
| no trunk group [1-8] | Remove trunk group [1-8] | Configure |

STORM CONTROL GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| storm-control broadcast enable | Enable the broadcast storm control | Configure |
| storm-control broadcast level [low ¦ mid ¦ high] | Set the broadcast storm control level | Configure |
| storm-control multicast enable | Enable the multicast storm control | Configure |
| storm-control multicast level [low ¦ mid ¦ high] | Set the multicast storm control level | Configure |
| storm-control unknown-unicast enable | Enable the unknown-unicast storm control | Configure |
| storm-control unknown-unicast level [low ¦ mid ¦ high] | Set the unknown-unicast storm control level | Configure |
| show storm-control broadcast | Display the broadcast storm control status | Configure |
| show storm-control broadcast level | Display the broadcast storm control level | Configure |
| show storm-control multicast | Display the multicast storm control status | Configure |

| show storm-control multicast level | Display the multicast storm control level | Configure |
| --- | --- | --- |
| show storm-control unknown-unicast | Display the unknown-unicast storm control status | Configure |
| show storm-control unknown-unicast level | Display the unknown-unicast storm control level | Configure |
| no storm-control broadcast | Disable the broadcast storm control | Configure |
| no storm-control broadcast level | Default the broadcast storm control to level high | Configure |
| no storm-control multicast | Disable the multicast storm control | Configure |
| no storm-control multicast level | Default the multicast storm control to level high | Configure |
| no storm-control unknown-unicast | Disable the unknown-unicast storm control | Configure |
| no storm-control unknown-unicast level | Default the unknown-unicast storm control to level high | Configure |

STATIC ROUTE GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ip route [IP_ADDR] [NETMASK:0-32] [NEXT_HOP] | Add static routing entry | Configure |
| ipv6 route [X:X::X:X/M] [X:X::X:X] | Set IPv6 Static Route | Configure |
| show ip route static | Display static routing entries | Configure |
| show ipv6 route | Display IPv6 Routing Table | Configure |
| show ipv6 route static | Display IPv6 Static Routing Table | Configure |
| no ip route [IP_ADDR] [NETMASK:0-32] | Delete a static routing entry | Configure |
| no ipv6 route [X:X::X:X/M] [X:X::X:X] | Remove an IPv6 Static Route entry | Configure |

OSPFV2 GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ip ospf authentication | Enable OSPF Authentication on this VLAN | VLAN |
| ip ospf authentication message-digest | Enable OSPF Authentication with MD5 on this VLAN | VLAN |
| ip ospf authentication-key [AUTH_KEY] | Set OSPF Authentication Password (Key) | VLAN |
| ip ospf dead-interval [1-65535] | Set OSPF Dead Interval; The default OSPF Dead Interval is 4 times hello interval | VLAN |
| ip ospf hello-interval [1-65535] | Set OSPF Hello Interval | VLAN |
| ip ospf message-digest-key [1-8] md5 [AUTH_KEY] | Set OSPF MD5 Authentication Password for KEY ID [1-8] | VLAN |
| ip ospf metric [1-65535] | Set OSPF Metric | VLAN |

| router ospf authentication area [AREA_ID] | Enable OSPF Authentication | Configure |
| --- | --- | --- |
| router ospf authentication message-digest area [AREA_ID] | Enable MD5 Authentication on specific OSPF Area | Configure |
| router ospf enable | Enable Global OSPF function | Configure |
| router ospf network [IP_ADDR] [NETMASK:0-32] [AREA_ID] | Set OSPF Network Interface and Area | Configure |
| router ospf router-id [ROUTER_ID] | Set OSPF Router-ID | Configure |
| show ip ospf authentication | Display OSPF Authentication on this VLAN | VLAN |
| show ip ospf authentication-key | Display OSPF Authentication Password (Key) | VLAN |
| show ip ospf dead-interval | Display OSPF Dead Interval | VLAN |
| show ip ospf hello-interval | Display OSPF Hello Interval | VLAN |
| show ip ospf message-digest-key | Display OSPF MD5 Authentication Password (Key) | VLAN |
| show ip ospf metric | Display OSPF Metric | VLAN |
| show router ospf | Display OSPF Routing Status | Configure |
| show router ospf authentication | Display OSPF Authentication Status | Configure |
| show router ospf mode | Display OSPF Enable/Disable | Configure |
| show router ospf neighbor | Display OSPF Routing Neighbor | Configure |
| show router ospf network | Display OSPF Network Interface and Area | Configure |
| show router ospf router-id | Display OSPF Router-ID | Configure |
| show router ospf vlan | Display OSPF Vlan Table | Configure |
| no ip ospf authentication | Disable OSPF Authentication on this VLAN | VLAN |
| no ip ospf authentication-key | Clear OSPF Authentication Password (Key) | VLAN |
| no ip ospf dead-interval | Clear OSPF Dead Interval | VLAN |
| no ip ospf hello-interval | Clear OSPF Hello Interval | VLAN |
| no ip ospf message-digest-key [1-8] | Remove OSPF MD5 Authentication Password for KEY ID [1-8] | VLAN |
| no ip ospf metric | Clear OSPF Metric | VLAN |
| no router ospf | Remove OSPF Routing Protocol Configuration | Configure |
| no router ospf authentication area [AREA_ID] | Disable OSPF Authentication on specific Area | Configure |
| no router ospf network [IP_ADDR] [NETMASK:0-32] | Clear OSPF Network Interface | Configure |
| no router ospf router-id | Clear OSPF Router-ID | Configure |

OSPFV3 GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| ipv6 ospf6 dead-interval [1-65535] | Set OSPFv3 Dead Interval; The default | VLAN |

|  | OSPF Dead Interval is 4 times hello interval |  |
| --- | --- | --- |
| ipv6 ospf6 hello-interval [1-65535] | Set OSPFv3 Hello Interval | VLAN |
| ipv6 ospf6 metric [1-65535] | Set OSPFv3 Metric | VLAN |
| ipv6 ospf6 network [broadcast ¦ point-to-point] | Set OSPFv3 Network-type | VLAN |
| ipv6 ospf6 priority [0-255] | Set OSPFv3 Priority | VLAN |
| router ospf6 area [AREA_ID] [X:X::X:X/M] | Set OSPFv3 Area | Configure |
| router ospf6 enable | Global OSPFv3 On | Configure |
| router ospf6 router-id [ROUTER_ID] | Set OSPFv3 Router-ID; OSPFv3 router-id is in IP address format: A.B.C.D | Configure |
| router ospf6 vlan [VLAN_id] [AREA_ID] | Set OSPFv3 interface/Area | Configure |
| show ipv6 ospf6 interface | Display OSPFv3 Information | Configure |
| show ipv6 ospf6 dead-interval | Display OSPFv3 Dead Interval | VLAN |
| show ipv6 ospf6 hello-interval | Display OSPFv3 Hello Interval | VLAN |
| show ipv6 ospf6 metric | Display OSPFv3 Metric | VLAN |
| show router ospf6 | Display OSPFv3 Routing Status | Configure |
| show router ospf6 mode | Display OSPFv3 Enable/Disable | Configure |
| show router ospf6 neighbor | Display OSPFv3 neighbor | Configure |
| show router ospf6 router-id | Display OSPFv3 Router-ID | Configure |
| show router ospf6 vlan | Display OSPFv3 VLAN Table | Configure |
| no router ospf6 | Remove OSPFv3 Routing Protocol Configuration | Configure |
| no router ospf6 vlan [VLAN_id] [AREA_ID] | Remove OSPFv3 interface/area | Configure |

RIPV1/V2 GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| router rip enable | Enable Global RIP function | Configure |
| router rip neighbor [IP_ADDR] | Set RIP Neighbors | Configure |
| router rip network [IP_ADDR] [NETMASK:0-32] | Set RIP Network | Configure |
| router rip timers [Update] [Time-out] [Garbage] | Set Routing-Table Update, Time-Out, and Garbage Collection Timers Default timer - update timer: 30s, time-out: 180s , garbage: 120s | Configure |
| router rip version [1¦2] | Set RIP Version | Configure |
| show router rip mode | Display RIP Enable/Disable | Configure |
| show router rip network | Show RIP Network Interface and Area | Configure |
| show router rip state | Show RIP Routing Table | Configure |
| show router rip status | Show RIP Status | Configure |
| no router rip | Remove RIP Configurations | Configure |

| no router rip neighbor | Clear RIP Router-ID | Configure |
| --- | --- | --- |
| no router rip network [IP_ADDR] [NETMASK:0-32] | Remove RIP Network Interface and Area | Configure |
| no router rip timers | Clear RIP Timers | Configure |
| no router rip version | Reset RIP Version | Configure |

RIPNG GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| router ripng enable | Enable Global RIP function | Configure |
| router ripng timers [Update] [Time-out] [Garbage] | Set Routing-Table Update, Time-Out, and Garbage Collection Timers Default timer - update timer: 30s, time-out: 180s , garbage: 120s | Configure |
| Router ripng vlan | Set RIPng Network | Configure |
| show router ripng mode | Display RIPng Enable/Disable | Configure |
| show router ripng state | Show RIPng Routing Table | Configure |
| show router ripng status | Show RIPng Status | Configure |
| no router ripng | Remove RIPng Routing Protocol Configurations | Configure |
| no router ripng vlan | Remove RIPng network-interface | Configure |

VRRP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| vrrp adv-timer [1-60] | Set Advertise Interval Timer of VRRP | VLAN |
| vrrp enable | Enable VRRP | VLAN |
| vrrp group-id [1-255] | Set Virtual Group ID of VRRP | VLAN |
| vrrp ip-address [Virtual IP address] | Set Virtual Server IP of VRRP | VLAN |
| vrrp preempt | Enable Preemption Mode of VRRP | VLAN |
| vrrp priority [1-254] | Set Priority of VRRP | VLAN |
| show vrrp-config |  | Configure |
| show vrrp adv-timer | Display Advertise Interval Timer of VRRP | VLAN |
| show vrrp all | Display All VRRP Configuration | VLAN |
| show vrrp group-id | Display Virtual Group ID of VRRP | VLAN |
| show vrrp ip-address | Display Virtual IP of VRRP | VLAN |
| show vrrp preempt | Display Preemption Mode of VRRP | VLAN |
| show vrrp priority | Display Priority of VRRP | VLAN |
| show vrrp state | Display State of VRRP | VLAN |

| no vrrp adv-timer | Disable VRRP and Remove Advertise Interval Timer of VRRP | VLAN |
| --- | --- | --- |
| no vrrp all | Disable VRRP and Remove All VRRP Configuration | VLAN |
| no vrrp group-id | Disable VRRP and Remove Virtual Group ID of VRRP | VLAN |
| no vrrp ip-address | Disable VRRP and Remove Virtual IP of VRRP | VLAN |
| no vrrp preempt | Disable Preemption Mode of VRRP | VLAN |
| no vrrp priority | Disable VRRP and Remove Priority of VRRP | VLAN |
| no vrrp state | Disable VRRP | VLAN |

802.1X GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| dot1x authentication server [1¦2] ip [IP] | Set 802.1X authentication server 1 or 2 address | Configure |
| dot1x authentication server [1¦2] port [PORT] | Set 802.1X authentication server 1 or 2 port | Configure |
| dot1x authentication server [1¦2] share-key [KEY] | Set 802.1X authentication server 1 or 2 share-key | Configure |
| dot1x authentication server type [local¦radius] | Set 802.1X authentication server type | Configure |
| dot1x enable | Enable 802.1X protocol | Configure |
| dot1x local-db [USER] [PASSWORD] | Set 802.1X local user database | Configure |
| dot1x authenticator enable | Set 802.1X authenticator | Interface |
| dot1x mode [mac-based ¦ port-based] | Set 802.1X mode as 1. MAC-based, 2.Port-based | Interface |
| dot1x reauthentication enable | Set 802.1X reauthentication | Interface |
| dot1x reauthentication period [60-65535] | Set 802.1X reauthentication period | Interface |
| show dot1x | Display 802.1X protocol state | Configure |
| show dot1x authentication server [1¦2] ip | Display 802.1X authentication server 1 or 2 address | Configure |
| show dot1x authentication server [1¦2] port | Display 802.1X authentication server 1 or 2 port | Configure |
| show dot1x authentication server [1¦2] share-key | Display 802.1X authentication server 1 or 2 key | Configure |
| show dot1x authentication server type | Display 802.1X authentication server type | Configure |
| show dot1x brief | Display 802.1X information | Configure |
| show dot1x local-db | Display 802.1X users and password in database | Configure |
| show dot1x server brief | Display 802.1X RADIUS server | Configure |

| show dot1x authenticator | Display 802.1X authenticator state | Interface |
| --- | --- | --- |
| show dot1x mode | Display 802.1X mode config | Interface |
| show dot1x reauthentication | Display 802.1X reauthentication state | Interface |
| show dot1x reauthentication period | Display 802.1X reauthentication period (in sec.) | Interface |
| no dot1x | Disable 802.1X protocol | Configure |
| no dot1x authentication server [1¦2] ip | Default 802.1X authentication server 1 or 2 address | Configure |
| no dot1x authentication server [1¦2] port | Default 802.1X authentication server 1 or 2 port | Configure |
| no dot1x authentication server [1¦2] share-key | Default 802.1X authentication server 1 or 2 share-key | Configure |
| no dot1x authentication server type | Default 802.1X authentication server type | Configure |
| no dot1x local-db [USER] | Remove an entry in 802.1X local database | Configure |
| no dot1x authenticator | Disable 802.1X authenticator | Interface |
| no dot1x mode | Default 802.1X mode as MAC-based | Interface |
| no dot1x reauthentication | Disable 802.1X reauthentication | Interface |
| no dot1x reauthentication period | Default 802.1X reauthentication period | Interface |

#### PORT MIRROR GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| mirror destination [DEST_PORT] | Set mirror interface of destination | Configure |
| mirror enable | Enable port mirror | Configure |
| mirror source [rx ¦ tx ¦ both] [PORT_LIST] | Set mirror interface of source | Configure |
| show mirror | Show port mirror enable/disable state | Configure |
| show mirror destination | Show port mirror destination configuration | Configure |
| show mirror source | Show port mirror source configuration | Configure |
| no mirror | Disable port mirror | Configure |
| no mirror destination | Delete port mirror Destination configuration | Configure |
| no mirror source | Delete port mirror Source configuration | Configure |

LLDP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| lldp enable | Enable LLDP protocol | Configure |
| lldp timer [5-32767] | Set LLDP timer | Configure |
| show lldp neighbor | Display LLDP neighbor | Configure |
| show lldp neighbor detail | Display LLDP neighbors in detail | Configure |
| show lldp state | Display LLDP status | Configure |

| show lldp timer | Display LLDP timer | Configure |
| --- | --- | --- |
| no lldp | Disable LLDP protocol | Configure |
| no lldp timer | Default LLDP timer | Configure |

#### SYSLOG GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| syslog local enable | Enable logging to local | Configure |
| syslog log clear | Clear syslog log | Configure |
| syslog remote enable | Enable logging to remote | Configure |
| syslog remote port [PORT] | Set syslog remote server port | Configure |
| syslog remote server [ADDRESS] | Set syslog remote server address | Configure |
| syslog usb enable | Enable log to USB device | Configure |
| show syslog local | Display local logging state | Configure |
| show syslog log | Display syslog messages | Configure |
| show syslog remote | Display remote logging state | Configure |
| show syslog remote port | Display remote server port | Configure |
| show syslog remote server | Display remote server IP | Configure |
| show syslog usb | Display USB logging state | Configure |
| no syslog local | Disable logging to local | Configure |
| no syslog remote | Disable logging to remote | Configure |
| no syslog remote port | Default syslog remote server port | Configure |
| no syslog remote server | Clear syslog remote server address | Configure |
| no syslog usb | Disable logging to USB | Configure |

SMTP GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| smtp authentication enable | Enable SMTP authentication | Configure |
| smtp authentication password [PASSWORD] | Set SMTP password | Configure |
| smtp authentication username [USER_NAME] | Set SMTP username | Configure |
| smtp enable | Enable SMTP | Configure |
| smtp receive [1-4] [RECEIVER_ADDRESS] | Set SMTP receiver [1-4] address | Configure |
| smtp sender [SMTP_SENDER_ADDRESS] | Set SMTP sender | Configure |
| smtp server address [SMTP_SERVER_ADDRESS] | Set SMTP server address | Configure |
| smtp server port [SMTP_SERVER_PORT] | Set SMTP server port | Configure |
| smtp subject [SUBJECT] | Set SMTP subject | Configure |
| show smtp authentication state | Display SMTP authentication status | Configure |
| show smtp authentication username | Display SMTP user name | Configure |
| show smtp receive [1-4] | Display SMTP receiver [1-4] | Configure |

| show smtp sender | Display SMTP sender | Configure |
| --- | --- | --- |
| show smtp server address | Display SMTP server address | Configure |
| show smtp server port | Display SMTP server port | Configure |
| show smtp state | Display SMTP service | Configure |
| show smtp subject | Display SMTP subject | Configure |
| no smtp authentication | Disable SMTP authentication | Configure |
| no smtp authentication password | Clear SMTP password | Configure |
| no smtp authentication username | Clear SMTP user name | Configure |
| no smtp | Disable SMTP | Configure |
| no smtp receive [1-4] | Clear SMTP receiver [1-4] | Configure |
| no smtp sender | Clear SMTP sender | Configure |
| no smtp server address | Clear SMTP server | Configure |
| no smtp server port | Clear SMTP server port | Configure |
| no smtp subject | Clear SMTP subject | Configure |

#### EVENT GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| event alarm ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Register a DDM event of current, Rx power, temperature, Tx power, or voltage | Configure |
| event alarm digital-input [high ¦ low] | Register an event of digital-input | Configure |
| event alarm interface [lan1-lanN] down | Register an event of Interface DOWN | Configure |
| event alarm [power1¦power2] | Register an event of power 1 or 2 failure | Configure |
| event smtp auth-failure | Register an event of authentication failure | Configure |
| event smtp cold-start | Register an event of cold-start | Configure |
| event smtp ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Register a DDM event of current, Rx power, temperature, Tx power, or voltage | Configure |
| event smtp digital-input [high ¦ low] | Register an event of digital-input | Configure |
| event smtp interface [lan1-lanN] down | Register an event of Interface DOWN | Configure |
| event smtp interface [lan1-lanN] up | Register an event of Interface UP | Configure |
| event smtp [power1¦power2] | Register an event of power 1 or 2 failure | Configure |
| event smtp warm-start | Register an event of warm-start | Configure |
| event snmptrap auth-failure | Register an event of authentication failure | Configure |
| event snmptrap cold-start | Register an event of cold-start | Configure |
| event snmptrap ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Register a DDM event of current, Rx power, temperature, Tx power, or voltage | Configure |
| event snmptrap digital-input [high ¦ low] | Register an event of digital-input | Configure |
| event snmptrap interface [lan1-lanN] down | Register an event of Interface DOWN | Configure |

| event snmptrap interface [lan1-lanN] up | Register an event of Interface UP | Configure |
| --- | --- | --- |
| event snmptrap [power1¦power2] | Register an event of power 1 or 2 failure | Configure |
| event snmptrap warm-start | Register an event of warm-start | Configure |
| event syslog auth-failure | Register an event of authentication failure | Configure |
| event syslog cold-start | Register an event of cold-start | Configure |
| event syslog ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Register a DDM event of current, Rx power, temperature, Tx power, or voltage | Configure |
| event syslog digital-input [high ¦ low] | Register an event of digital-input | Configure |
| event syslog interface [lan1-lanN] down | Register an event of Interface DOWN | Configure |
| event syslog interface [lan1-lanN] up | Register an event of Interface UP | Configure |
| event syslog [power1¦power2] | Register an event of power 1 or 2 failure | Configure |
| event syslog warm-start | Register an event of warm-start | Configure |
| show event alarm ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Display current, Rx power, temperature, Tx power, or voltage event registration | Configure |
| show event alarm digital-input | Display digital-input event registration | Configure |
| show event alarm interface [lan1-lanN] down | Display interface DOWN event registration | Configure |
| show event alarm [power1¦power2] | Display power 1 or 2 event registration | Configure |
| show event smtp auth-failure | Display authentication failure event registration | Configure |
| show event smtp cold-start | Display cold-start event registration | Configure |
| show event smtp ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Display current, Rx power, temperature, Tx power, or voltage event registration | Configure |
| show event smtp digital-input | Display digital-input event registration | Configure |
| show event smtp interface [lan1-lanN] down | Display interface DOWN event registration | Configure |
| show event smtp interface [lan1-lanN] up | Display interface UP event registration | Configure |
| show event smtp [power1¦power2] | Display power 1 or 2 event registration | Configure |
| show event smtp warm-start | Display warm-start event registration | Configure |
| show event snmptrap auth-failure | Display authentication failure event registration | Configure |
| show event snmptrap cold-start | Display cold-start event registration | Configure |
| show event snmptrap ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Display current, Rx power, temperature, Tx power, or voltage event registration | Configure |
| show event snmptrap digital-input | Display digital-input event registration | Configure |
| show event snmptrap interface [lan1-lanN] down | Display interface DOWN event registration | Configure |
| show event snmptrap interface [lan1-lanN] up | Display interface UP event registration | Configure |

| show event snmptrap [power1¦power2] | Display power 1 or 2 event registration | Configure |
| --- | --- | --- |
| show event snmptrap warm-start | Display warm-start event registration | Configure |
| show event syslog auth-failure | Display authentication failure event registration | Configure |
| show event syslog cold-start | Display cold-start event registration | Configure |
| show event syslog ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Display current, Rx power, temperature, Tx power, or voltage event registration | Configure |
| show event syslog digital-input | Display digital-input event registration | Configure |
| show event syslog interface [lan1-lanN] down | Display interface DOWN event registration | Configure |
| show event syslog interface [lan1-lanN] up | Display interface UP event registration | Configure |
| show event syslog [power1¦power2] | Display power 1 or 2 event registration | Configure |
| show event syslog warm-start | Display warm-start event registration | Configure |
| no event alarm ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Unregister a DDM event of current, Rx power, temperature, Tx power, or voltage | Configure |
| no event alarm digital-input | Unregister an event of digital-input | Configure |
| no event alarm interface [lan1-lanN] down | Unregister an event of Interface DOWN | Configure |
| no event alarm [power1¦power2] | Unregister an event of power 1 or 2 failure | Configure |
| no event smtp auth-failure | Unregister an event of authentication failure | Configure |
| no event smtp cold-start | Unregister an event of cold-start | Configure |
| no event smtp ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Unregister a DDM event of current, Rx power, temperature, Tx power, or voltage | Configure |
| no event smtp digital-input | Unregister an event of digital-input | Configure |
| no event smtp interface [lan1-lanN] down | Unregister an event of Interface DOWN | Configure |
| no event smtp interface [lan1-lanN] up | Unregister an event of Interface UP | Configure |
| no event smtp [power1¦power2] | Unregister an event of power 1 or 2 failure | Configure |
| no event smtp warm-start | Unregister an event of warm-start | Configure |
| no event snmptrap auth-failure | Unregister an event of authentication failure | Configure |
| no event snmptrap cold-start | Unregister an event of cold-start | Configure |
| no event snmptrap ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Unregister a DDM event of current, Rx power, temperature, Tx power, or voltage | Configure |
| no event snmptrap digital-input | Unregister an event of digital-input | Configure |
| no event snmptrap interface [lan1-lanN] down | Unregister an event of Interface DOWN | Configure |
| no event snmptrap interface [lan1-lanN] up | Unregister an event of Interface UP | Configure |
| no event snmptrap [power1¦power2] | Unregister an event of power 1 or 2 failure | Configure |

| no event snmptrap warm-start | Unregister an event of warm-start | Configure |
| --- | --- | --- |
| no event syslog auth-failure | Unregister an event of authentication failure | Configure |
| no event syslog cold-start | Unregister an event of cold-start | Configure |
| no event syslog ddm [lanX-lanY] [current ¦ rx_power ¦ temperature ¦ tx_power ¦ voltage] | Unregister a DDM event of current, Rx power, temperature, Tx power, or voltage | Configure |
| no event syslog digital-input | Unregister an event of digital-input | Configure |
| no event syslog interface [lan1-lanN] down | Unregister an event of Interface DOWN | Configure |
| no event syslog interface [lan1-lanN] up | Unregister an event of Interface UP | Configure |
| no event syslog [power1¦power2] | Unregister an event of power 1 or 2 failure | Configure |
| no event syslog warm-start | Unregister an event of warm-start | Configure |

MAC ADDRESS TABLE GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| clear mac address-table dynamic | Flush dynamic MAC addresses in MAC table | Configure |
| mac address add [VID: 1-4094] [MAC_ADDR] [PORT] | Set a MAC address to MAC table | Configure |
| show mac address | Display MAC table | Configure |
| no mac address [VID: 1-4094] [MAC_ADDR] | Remove a MAC address from FDB | Configure |

USB GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| usb auto-backup | Auto save to USB if running config is changed | Configure |
| usb auto-load | Auto load config from USB to switch | Configure |
| show usb auto-backup | Display USB auto backup activated status | Configure |
| show usb auto-load | Display USB auto load activated status | Configure |
| no usb auto-backup | Disable auto save | Configure |
| no usb auto-load | Disable auto load | Configure |

#### FILE GROUP

| Command | Explanation | Mode |
| --- | --- | --- |
| copy running-config startup-config | Save running-config to startup-config | Configure |
| copy running-config usb [file] | Save running-config to USB | Configure |
| copy startup-config running-config | Restore from startup-config | Configure |
| copy usb firmware [file] | Upgrade firmware from USB | Configure |
| copy startup-config usb [file] | Save startup-config to USB | Configure |

| copy usb startup-config [file] | Restore startup-config from USB | Configure |
| --- | --- | --- |
| upload file name [FILE_NAME] | Set uploading file name | Configure |
| upload server ip [SERVER_IP] | Set uploading server IP | Configure |
| upload tftp | Upload and update firmware via TFTP (slower) | Configure |
| upload wget | Upload and update firmware via HTTP (faster) | Configure |
| show upload file name | Display uploading file name | Configure |
| show upload server ip | Display uploading server IP | Configure |
| no upload file name | Default uploading file name | Configure |
| no upload server ip | Clear uploading server IP | Configure |